## Cover (hidden)
GRID CONNECTIVITY COMPLIANCE WORKBOOK
CON4 – RE Plant Compliance Checklist
Central Transmission Utility ¦ Grid-India ¦ RE Plant DMAT Submission
PROJECT DETAILS |  | DOCUMENT DETAILS
Project Name / Grantee: | Rajasthan Solar Park – Phase II | Document Version: | v1.2
CTU Application No.: | CTU/GNA/2024/1547 | Prepared By: | Gaurav Sharma, PE
Connectivity Quantum (MW): | 500 | Reviewed By: | Anjali Mehta, Sr. Engineer
POI Station (ISTS): | Bikaner ISTS 765/400 kV | Approved By: | Rakesh Verma, DGM
POI Bus Voltage (kV): | 400 kV | Submission Date: | 15-Mar-2025
RE Plant Type: | Solar PV (IBR) – without BESS | Revision No.: | Rev-3
Expected COD: | 15-Jun-2026 / 30-Sep-2026 | Study Engineer: | Sanjay Patel
IBR OEM: | SMA Solar Technology AG | Organization: | Grid-India Connectivity Cell
COLOUR CODE LEGEND
| Editable Input Cell | Fill in with project/study data
| Developer / Auto-populated | Pre-filled reference or formula
| Compliant / Achieved | Value meets the required limit
| Non-Compliant / Inconsistent | Value does not meet limit or inconsistent
| Not Applicable / Blank | Row not applicable or data not available
This workbook is prepared for DMAT compliance submission under CTU/Grid-India connectivity regulations for RE Plants.

## Summary Dashboard (hidden)
COMPLIANCE SUMMARY DASHBOARD
CON4 – RE Plant DMAT Compliance Status Overview
COMPLIANCE SCORECARD
General Details 0/27 Items |  | TD Requirements 1/140 Items |  | Power Quality 0/15 Items |  | Steady State 0/60 Items
Awaited |  | 1 Submitted |  | Awaited |  | Awaited
Dynamic Data 0/99 Items |  | Test Cases 0/238 Items
Awaited |  | Awaited
SHEET-WISE COMPLIANCE SUMMARY TABLE
Sheet / Category | Total Items | Submitted | Not Submitted | Compliance % | Priority | Status | Remarks
General Details - RE | 27 | 25 |  |  | HIGH | On Track | 25/27 submitted; 2 items pending
TD Requirements - RE | 140 | 40 |  |  | HIGH | Pending | 40 submitted; 100 docs from OEM pending
Power Quality | 15 | 15 |  |  | HIGH | On Track | All 15 items compliant ✓
Steady State Analysis | 60 | 38 |  |  | HIGH | In Progress | 38 values filled; 22 PSS/E values pending
Dynamic Data - RE | 99 | 39 |  |  | HIGH | Pending | 39 LVRT/HVRT values filled; 60 pending
Standard Test Cases | 238 | 80 |  |  | MEDIUM | Pending | 80 test files submitted; 158 awaited
TOTAL | 579
NOTES ON COLOUR CODING USED THROUGHOUT THIS WORKBOOK
| Input/Editable Cell |  | Yellow highlight — Developer/entity must fill in this data
| Developer Reference |  | Blue highlight — Pre-filled by developer or reference data
| Compliant / Achieved |  | Green highlight — Value observed meets or exceeds the required limit
| Non-Compliant / Inconsistent |  | Red/Orange highlight — Value does not meet limit or data is inconsistent

## Pivot Analysis (hidden)
CON4 COMPLIANCE PIVOT ANALYSIS — Rajasthan Solar Park Phase II ¦ 500 MW Solar IBR
Submission cut-off: 15-Mar-2025 ¦ Study Engineer: Gaurav Sharma ¦ POI: Bikaner 765/400 kV ISTS ¦ Auto-generated summary
SECTION 1 – SHEET-WISE SUBMISSION OVERVIEW
Sheet / Category | Total Items | Submitted | Pending | Completion % | Remarks
General Details - RE |  |  |  |  | 2 items pending developer input
TD Requirements - RE |  |  |  |  | 100 TD docs awaiting OEM
Power Quality |  |  |  |  | All PQ parameters compliant ✓
Steady State Analysis |  |  |  |  | 22 PSS/E LF values pending
Dynamic Data - RE |  |  |  |  | 60 LVRT/HVRT params pending
Standard Test Cases |  |  |  |  | 158 test result files awaited
TOTAL
SECTION 2 – TD REQUIREMENT CATEGORY BREAKDOWN
Category | Total | Submitted | Pending | Completion % | RAG
Technical Details - IBR Unit
Single Line Diagram
Equipment details
Certification & Unit level testing to be furnished by the entity
Unit Level Reports (Inverter)
Unit Level Reports [SVG (if applicable)]
Unit Level Reports (WTG)
Unit Level Reports (BESS/PCS) (if applicable)
PPC
Plant Level Study Reports
Plant Level RMS Files (PSS/E)
Plant Level EMT Models(PSCAD)
Plant Level RMS Models(PSS/E)
SECTION 3 – POWER QUALITY COMPLIANCE STATUS
Parameter | Category | Value Observed | Limit | Compliance Status
TDD – Max Harmonic Current Distortion | Harmonics |  |  | COMPLIANT ✓
THD 2 ≤ h < 11 | Harmonics |  |  | COMPLIANT ✓
THD 11 ≤ h < 17 | Harmonics |  |  | COMPLIANT ✓
THD 17 ≤ h < 23 | Harmonics |  |  | COMPLIANT ✓
THD 23 ≤ h < 35 | Harmonics |  |  | COMPLIANT ✓
DC Current Injection | DC Injection |  |  | COMPLIANT ✓
Flicker – Short Term (Pst) | Flicker |  |  | COMPLIANT ✓
Flicker – Long Term (Plt) | Flicker |  |  | COMPLIANT ✓
Voltage Unbalance (IEC 61000-4-30) | V. Quality |  |  | COMPLIANT ✓
SECTION 4 – DYNAMIC PERFORMANCE SUMMARY (LVRT / HVRT)
Test Condition | Tool | Incremental IQ (pu) | Active Current (pu) | Active Pwr Recovery (%) | Limit (%) | Status
LVRT 0.15 pu, 100% P, Sym | PSS/E |  |  | 93.2 | ≥90 | COMPLIANT ✓
LVRT 0.15 pu, 100% P, Sym | PSCAD |  | 0.79 | 92.8 | ≥90 | COMPLIANT ✓
LVRT 0.5 pu, 100% P, Sym | PSS/E | 0.95 | 0.75 | 93.2 | ≥90 | COMPLIANT ✓
LVRT 0.85 pu, 100% P, Sym | PSS/E | 0.48 | 0.88 | — | — | No trip – PASS ✓
HVRT 1.1 pu, 100% P, Sym | PSS/E | — | — | — | — | No trip – PASS ✓
HVRT 1.3 pu, 100% P, Sym | PSS/E | — | — | — | — | No trip – PASS ✓
SECTION 5 – KEY GAPS & ACTION ITEMS
# | Area | Gap Description | Items Missing | Priority | Responsible | Target Date | Status
1 | TD Requirements | 100 TD documents pending OEM submission | 100 | HIGH | Developer / OEM | 15-Apr-2025 | OPEN
2 | Standard Tests | 158 test result files not yet provided | 158 | HIGH | Developer / OEM | 30-Apr-2025 | OPEN
3 | Steady State | 22 PSS/E load flow observed values missing | 22 | HIGH | Study Engineer | 20-Mar-2025 | IN PROGRESS
4 | Dynamic Data | 60 LVRT/HVRT/DMAT parameter values unfilled | 60 | HIGH | Study Engineer | 25-Mar-2025 | IN PROGRESS
5 | General Details | 2 general items awaiting developer input | 2 | MEDIUM | Developer | 10-Mar-2025 | IN PROGRESS
6 | Documentation | CONN-TD4 final signature pending | 1 | MEDIUM | Developer/Legal | 01-Mar-2025 | NEAR CLOSURE
SECTION 6 – OVERALL SCORECARD
Overall Submission Rate
Power Quality | 100% (15/15) – All parameters within limits | COMPLIANT
Dynamic Performance (LVRT/HVRT) | Active Power Recovery >90% confirmed | COMPLIANT
Documentation Completeness | 342 items pending – OEM & Study Engineer action needed | ACTION NEEDED

## General Details-RE
General Details for Renewable Energy Source
Sr. No. | Category | Description | Unit | Details | Submission Status (Submitted/ Awaited) | Name of File/ Folder Name | Found? - Name of File/ Folder Name | Remarks on Files Found | 📝 Developer Guidance / Explanatory Note
1 | General | Name of Connectivity Grantee | Name | M/s VEH Green Energy Pvt. Ltd. | Submitted | 27. Connectivity Documents Compliance sheet & Agreements\CONN-TD-1_R1_VEHGEPL_2200000126 & 2200002094 | Yes | Found | Enter the full legal name of the entity that holds the CTU Connectivity/GNA grant. Must match exactly as on the grant letter. Example: 'Rajasthan Solar Park – Phase II'.
2 | General | CTU Connectivity / GNA Application Number | Number | Wind - CTU/S/5/Conn/INT-1C-2200000126 Solar - CTU/SR/CONN-INT-2B/2200002094 | Submitted | 27. Connectivity Documents Compliance sheet & Agreements\CONN-TD-1_R1_VEHGEPL_2200000126 & 2200002094 | Yes | Found | Enter the CTU-assigned application number. Obtain from your CTU grant letter. Example: 'CTU/GNA/2024/1547'.
3 | General | Connectivity Quantum (MW) Granted | MW | 153.6 | Submitted | 27. Connectivity Documents Compliance sheet & Agreements\Final_Grant_Connectivity | Yes | Found | Connectivity quantum (in MW) as per the grant letter. Do NOT change to installed capacity – use exactly what is stated in the grant. Example: '500 MW'.
4 | General | Installed capacity as per Connectivity (MW) | MW | 207.8 | Submitted | 27. Connectivity Documents Compliance sheet & Agreements\CONN-TD-1_R1_VEHGEPL_2200000126 & 2200002094 | Yes | Found | Installed capacity (MW) as per connectivity approval / design documents.
5 | General | Installed rated capacity as per models (MW) | MW | 207.8 | Submitted | 15. PSSE Steady State Report | Yes | Found | Installed capacity (MW) as modelled in PSS/E or PSCAD.
7 | General | Installed Capacity (in MW) with Breakup of different sources for Hybrid | Solar/Wind/ESS etc. | Solar: 52.8 MW Wind: 155 MW | Submitted | 27. Connectivity Documents Compliance sheet & Agreements\Final_Grant_Connectivity | Yes | Found | For hybrid plants, breakup capacity of each source alongwith totals (Solar MW / Wind MW / ESS MWh).Format 'Solar: <X> MW'., 'Wind: <X> MW' Source: Project capacity documents.
8 | General | Connection Details (CONN-TD 4) Quantum applied for: | MW | 153.6 | Submitted | 27. Connectivity Documents Compliance sheet & Agreements\Final_Grant_Connectivity | Yes | Found | Quantum applied for under CONN-TD 4 form.
9 | General | CEA Registration Number | Number | 1400007949 ( for 153.6MW Wind ) 1400014697 (for 52.8MW Solar ) | Submitted | 27. Connectivity Documents Compliance sheet & Agreements\CONN-TD-1_R1_VEHGEPL_2200000126 & 2200002094 | Yes | Found | CEA Registration Number as issued by Central Electricity Authority for this RE plant. Attach the CEA Registration Certificate.
10 | General | Type of RE Plant (Solar/Wind/Hybrid/with or without BESS) | Number | Hybrid ( Solar and Wind) | Submitted | 27. Connectivity Documents Compliance sheet & Agreements\CONN-TD-1_R1_VEHGEPL_2200000126 & 2200002094 | Yes | Found | Select the appropriate type: 'Solar PV (IBR)', 'Wind (IBR)', 'Hybrid – Solar + Wind', 'Solar with BESS', etc. Be specific about IBR type and BESS inclusion.
11 | General | ISTS Station (POI bus) | Name | 765/400/220 kV Koppal-II ISTS SS. | Submitted | 27. Connectivity Documents Compliance sheet & Agreements\CONN-TD-1_R1_VEHGEPL_2200000126 & 2200002094 | Yes | Found | Name of ISTS substation where grid connection (POI) is established. Format: '<Substation Name> <kV>/<kV> ISTS'. Example: 'Bikaner 765/400 kV ISTS'.
12 | General | POI Bus Voltage | kV | 220 | Submitted | 27. Connectivity Documents Compliance sheet & Agreements\CONN-TD-1_R1_VEHGEPL_2200000126 & 2200002094 | Yes | Found | POI Bus voltage level in kV (the voltage at the Point of Interconnection). Typical values: 400 kV, 220 kV, 132 kV. Must match SLD.
13 | General | Expected Date of First COD/Final COD | Date | 2026-06-30 | Submitted | 27. Connectivity Documents Compliance sheet & Agreements\CONN-TD-1_R1_VEHGEPL_2200000126 & 2200002094 | Yes | Found | Provide expected dates in DD-Mon-YYYY format. First COD = first unit energisation, Final COD = full plant. Example: '15-Jun-2026 / 30-Sep-2026'.
14 | General | IBR Makes / Name of OEM | Name | Wind Turbine Generator- Envision Energy India Pvt.Ltd. Inverter - Sineng Electric India Pvt.Ltd. SVG - TBEA Xi'an Electric Technology co.,Ltd. | Submitted | 3. Datasheets of all the equipment | Yes | Found | Full name of the Inverter/IBR OEM. Example: 'SMA Solar Technology AG', 'Sungrow Power Supply Co.', 'ABB Ltd.'. Must match type test report.
15 | General | Name of OEM (WTG) | Name | Envision Energy India Pvt.Ltd. | Submitted | 3. Datasheets of all the equipment | Yes | Found | Applicable for wind plants only. Enter WTG OEM name. For pure solar, enter 'N/A (Solar only)'.
16 | General | Name of OEM (SVG) | Name | TBEA Xi'an Electric Technology co.,Ltd. | Submitted | 3. Datasheets of all the equipment | Yes | Found | Applicable if SVG/STATCOM is installed. Enter OEM name. For no SVG, enter 'N/A'. Example: 'Statcon Energiaa', 'GE Grid Solutions'.
17 | General | Name of OEM (BESS/PCS) | Name | NA | Submitted |  |  |  | Applicable if BESS/PCS is installed. Enter OEM name. For no BESS, enter 'N/A'.
18 | General | Name of OEM (PPC) | Name | EIT AUTOMATION Pvt.Ltd. | Submitted | 3. Datasheets of all the equipment | Yes | Found | PPC (Power Plant Controller) OEM and model. Example: 'ABB PPC-9000', 'Siemens MGMS', 'Ingeteam INGECON'. Attach OEM datasheet.
19 | General | Capacity (MVAr) & Resonant ferquency of filter (1st) (if applicable) | MVAR, Hz | NA | Submitted |  |  |  | If harmonic filters are installed, enter: Reactive power rating in MVAr and resonant (tuning) frequency in Hz. Example: '25 MVAr, 150 Hz (3rd harmonic)'. Enter 'N/A' if no filter.
20 | General | Capacity (MVAr) & Resonant ferquency of filter (2nd) (if applicable) | MVAR, Hz | 1.6MVAr,33kV,2nd Order ST ( Tuning Frequency : 198Hz) | Submitted | 3. Datasheets of all the equipment | Yes | Found | Second harmonic filter details (if installed). Same format as Sr.18. Enter 'N/A' if not applicable.
21 | General | Capacity (MVAr) & Resonant ferquency of filter (3rd) (if applicable) | MVAR, Hz | NA | Submitted |  |  |  | Third harmonic filter details (if installed). Enter 'N/A' if not applicable.
22 | General | SVG Rating (MVAR, if applicable) | MVAR | 2 x 30 MVAr | Submitted | 3. Datasheets of all the equipment | Yes | Found | SVG rating in MVAr if installed. Specify +/- range. Example: '±60 MVAr'. Attach SVG technical datasheet. Enter 'N/A' if not installed.
23 | General | IBR Model Name/No. | Name | Wind Turbine Generator- EN 182/5.0 Inverter - EP-3300-HB-UD SVG - TSVG-30/33-W-C | Submitted | 3. Datasheets of all the equipment | Yes | Found | IBR model name/number as per OEM datasheet. Example: 'SMA SunCentral 2500 kVA', 'Sungrow SG3125HV'. Must match type test report.
24 | General | Rated IBR Capacity | MVA,, Volts. Deg C | Wind Turbine Generator - 5.0MW Inverter - 3300kVA@50°C SVG - 30MVAr | Submitted | 3. Datasheets of all the equipment | Yes | Found | IBR rating in format 'MVA, voltage, Temperature'. Example: '2500 kVA, 690 V, 50 deg C'. Source: OEM technical datasheet. If multiple OEMs exist, please enter their data in the same cell.
25 | General | Number of IBRs | Number | Wind Turbine Generator - 31 Nos. Inverter - 16 Nos. SVG - 2 Nos. | Submitted | 3. Datasheets of all the equipment | Yes | Found | Total count of IBR units in the plant. Example: '200 units'. Must be consistent with total plant capacity ÷ unit rating.
26 | General | Site temperature considered for plant compliance as per CEA Procedure for assessment of the Design Temperature for RE Plants | Degrees | 44 °C | Submitted | 15. PSSE Steady State Report | Yes | Found | As per CEA Procedure for Design Temperature Assessment of RE Plants. Obtain from nearest IMD station data or CEA temperature map. Enter in °C. Example: '45 °C'.
27 | General | Signed CONNTD-1 submitted? | Yes/No | Yes | Submitted | 27. Connectivity Documents Compliance sheet & Agreements\CONN-TD-1_R1_VEHGEPL_2200000126 & 2200002094 | Yes | Found | Confirm if the signed CONN-TD 1 form has been submitted to CTU. Enter 'Yes' or 'No'.
| General | Steady State Scenarios for hybrid projects submitted as per CTU advisory dated 20.11.2025 | Yes/No | Yes | Submitted | 14. PSSE Detailed Model | Yes | Found | Applicable for hybrid plants only. If pure solar or pure wind, enter 'Not Applicable'. If hybrid, submit simultaneous power injection study report as per CTU advisory.
| General | Dynamic Scenarios for hybrid projects submitted as per CTU advisory dated 20.11.2025 | Yes/No | Yes | Submitted | 17. PSSE Dynamic Report | Yes | Found | Applicable for hybrid plants only. If pure solar or pure wind, enter 'Not Applicable'. If hybrid, submit simultaneous power injection study report as per CTU advisory.
| General | Power Quality Scenarios for hybrid projects submitted as per CTU advisory dated 20.11.2025 | Yes/No | Yes | Submitted | 20. PSCAD Power Quality Report | Yes | Found | Applicable for hybrid plants only. If pure solar or pure wind, enter 'Not Applicable'. If hybrid, submit simultaneous power injection study report as per CTU advisory.
28 | General | Nearest Loaction of IMD Station for Power Plant | latitude, longitude | 15.2° N, 76° E | Submitted |  |  |  | Coordinates of nearest IMD (India Meteorological Department) station used for temperature data. Format: 'DD.DDNB, DD.DDE'. Example: '27.25N, 73.01E'. Source: IMD station reference document.
|  | CEA Site Temperature at the location | deg Celsius | 42.6 | Submitted | 15. PSSE Steady State Report | Yes | Found
The Applicant is required to fill in yellow-highlighted cells only. All remaining fields are system-locked and pre-populated for reference.
⚠ IMPORTANT DISCLAIMER — INDICATIVE SHEET ONLY This workbook is prepared as an indicative checklist to assist the Applicant/Developer in organising submission data for CTU/Grid-India CON4 compliance. The values, limits, and compliance flags shown herein are for self-assessment purposes ONLY. Submission of this sheet or attainment of values that are numerically within the limits indicated does NOT, by itself, constitute or guarantee regulatory compliance. Final compliance determination rests solely with CTU / Grid-India as per applicable regulations, grid codes, and CEA standards. The Developer must independently verify all parameters against the latest applicable CEA Connectivity Regulations, Grid Code, and CTU/Grid-India circulars/advisory.

## Steady State
Steady State Simulation Results for Renewable Energy Sources
Sl No | Category | Description | Unit | Voltage at POI | Mathematical Notation | Value Observed | Lower Limit | Upper Limit | Ref Document Name | Found? - Ref Document Name | Remarks on Files Found | Page number of the document | Remarks | 📝 Developer Guidance / Explanatory Note
1 | General | Maximum(Peak) Transformer Loading Observed Across All Simulation Scenarios wrt Name Plate Rating | % |  |  | 84 | 100 | 100 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 49 |  | Maximum transformer (power transformer / ICT) loading across ALL PSS/E load flow scenarios. Enter in %. Limit: ≤100%.Source: PSS/E LF Report.
2 | General | Maximum IDT/Lines/Cables Loading of all Cases wrt Name Plate Rating | % |  |  | 88 | 100 | 100 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 65 |  | Maximum IBR unit transformer (IDT) loading w.r.t. nameplate rating across all cases. Enter in %. Limit: ≤100%. Source: PSS/E LF Report.
| General | Maximum Loading Power Cables/Distribution Lines of all Cases wrt Name Plate Rating | % |  |  | 92 | 100 | 100 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 49 |  | Maximum % loading of any power cable or distribution line in the internal plant network across all load flow scenarios. Limit: ≤100%. Source: PSS/E Load Flow Report.
3 | General | Maximum Inverter/WTG Loading at site temperature as per CEA Procedure | MVA |  |  | 100 | 100 | 100 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 49 |  | Maximum inverter/WTG MVA output considering temperature derating at site temperature (as per CEA procedure). Enter in MVA. Source: CEA Temperature Procedure + PSS/E model.
7 | General | Maximum Voltage Observed at Plant bus | p.u. |  |  | 1.0999 | 1.1 | 1.1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Maximum voltage (p.u.) observed at the plant POI bus across all steady-state scenarios. Limit: ≤1.05 p.u. Check especially at light load / leading PF conditions. Source: PSS/E LF Report.
8 | General | Minimum Voltage Observed at Plant bus | p.u. |  |  | 0.9209 | 0.9 | 0.9 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Minimum voltage (p.u.) observed at plant POI bus across all scenarios. Limit: ≥0.95 p.u. Check especially at full load lagging PF. Source: PSS/E LF Report.
12 | General | Reactive Power Injection in pu(100MVA base) at PoI, Unity PF, Voltage at POI 1.0 pu | p.u. | 1 | Q_POI | 0.01 |  |  | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Net reactive power injection at POI (100 MVA base) for Unity PF, 1.0 pu voltage scenario. Expected: ≈0.00 p.u. (since unity PF means no reactive injection). Source: PSS/E LF case output.
13 | General | Unity PF, Voltage at POI 1.0 pu(plant level): Inverter P(pu) | p.u. | 1 | P_INV | 0.27 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter active power output (p.u. on 100 MVA base) for Unity PF, 1.0 pu voltage case Source: PSS/E load flow output.
14 | General | Unity PF, Voltage at POI 1.0 pu: Inverter Q(pu) | p.u. | 1 | Q_INV | 0 | -1 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter reactive power output (p.u.) for Unity PF, 1.0 pu voltage case Source: PSS/E load flow output.
16 | General | Unity PF, Voltage at POI 1.0 pu: SVG Q(pu) | p.u. | 1 | Q_SVG | 1 | -1 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | SVG reactive power (p.u.) for Unity PF, 1.0 pu voltage case.Source: PSS/E load flow output.
17 | General | Unity PF, Voltage at POI 1.0 pu: WTG P(pu) | p.u. | 1 | P_WTG | 1 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG active power (p.u.) for Unity PF, 1.0 pu case. Enter 'N/A' if no WTG (pure solar). Source: PSS/E output.
18 | General | Unity PF, Voltage at POI 1.0 pu: WTG Q(pu) | p.u. | 1 | Q_WTG | 0 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG reactive power (p.u.) for Unity PF, 1.0 pu case. Enter 'N/A' if no WTG. Source: PSS/E output.
17 | General | Unity PF, Voltage at POI 1.0 pu: BESS P(pu) | p.u. | 1 | P_WTG | N/A | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG active power (p.u.) for Unity PF, 1.0 pu case. Enter 'N/A' if no WTG (pure solar). Source: PSS/E output.
18 | General | Unity PF, Voltage at POI 1.0 pu: BESS Q(pu) | p.u. | 1 | Q_WTG | N/A | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG reactive power (p.u.) for Unity PF, 1.0 pu case. Enter 'N/A' if no WTG. Source: PSS/E output.
33 | General | Reactive Power Injection in pu(100MVA base) at PoI, Unity PF, Voltage at POI 0.95 pu | p.u. | 0.95 | Q_POI | -0.01 | 0 | 1.643 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Net Q at POI for Unity PF, 0.95 pu voltage scenario. Expected: ≈0.00 p.u. Source: PSS/E LF output. Low voltage scenario tests plant behaviour under under-voltage grid conditions.
34 | General | Unity PF, Voltage at POI 0.95 pu: Inverter P(pu) | p.u. | 0.95 | P_INV | 0.28 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter P for Unity PF, 0.95 pu POI voltage scenario. Source: PSS/E output.
35 | General | Unity PF, Voltage at POI 0.95 pu: Inverter Q(pu) | p.u. | 0.95 | Q_INV | 0 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter Q for Unity PF, 0.95 pu voltage. Should be ≈0 (unity PF). Source: PSS/E output.
36 | General | Unity PF, Voltage at POI 0.95 pu: SVG P(pu) | p.u. | 0.95 |  | 0.000 | 0 | 1 | PSS/E LF Report.pdf | No | Missing: PSS/E LF Report.pdf | 25 |  | SVG P for Unity PF, 0.95 pu voltage. Source: PSS/E output.
37 | General | Unity PF, Voltage at POI 0.95 pu: SVG Q(pu) | p.u. | 0.95 | Q_SVG | 1 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | SVG Q for Unity PF, 0.95 pu voltage. Source: PSS/E output.
38 | General | Unity PF, Voltage at POI 0.95 pu: WTG P(pu) | p.u. | 0.95 | P_WTG | 1 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG P for Unity PF, 0.95 pu voltage. 'N/A' for solar. Source: PSS/E output.
39 | General | Unity PF, Voltage at POI 0.95 pu: WTG Q(pu) | p.u. | 0.95 | Q_WTG | 0 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG Q for Unity PF, 0.95 pu voltage. 'N/A' for solar. Source: PSS/E output.
40 | General | Reactive Power Injection in pu(100MVA base) at PoI, 0.95 Lagging, Voltage at POI 0.95 pu | p.u. | 0.95 | Q_POI | 0.33 | 0 | 1.643 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Net Q at POI for 0.95 Lag, 0.95 pu voltage. Enter actual simulation value. The low voltage condition stresses reactive capability. Source: PSS/E LF output.
41 | General | 0.95 Lagging, Voltage at POI 0.95 pu: Inverter P(pu) | p.u. | 0.95 | P_INV | 0.26 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter P for 0.95 Lag, 0.95 pu case. Source: PSS/E output.
42 | General | 0.95 Lagging, Voltage at POI 0.95 pu: Inverter Q(pu) | p.u. | 0.95 | Q_INV | 0.4 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter Q for 0.95 Lag, 0.95 pu case. Should be ≈+0.329 p.u. Source: PSS/E output.
43 | General | 0.95 Lagging, Voltage at POI 0.95 pu: SVG P(pu) | p.u. | 0.95 |  | 0.001 | 0 | 1 | PSS/E LF Report.pdf | No | Missing: PSS/E LF Report.pdf | 35 |  | SVG P for 0.95 Lag, 0.95 pu case. Source: PSS/E output.
44 | General | 0.95 Lagging, Voltage at POI 0.95 pu: SVG Q(pu) | p.u. | 0.95 | Q_SVG | 1 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | SVG Q for 0.95 Lag, 0.95 pu case. Source: PSS/E output.
45 | General | 0.95 Lagging, Voltage at POI 0.95 pu: WTG P(pu) | p.u. | 0.95 | P_WTG | 1 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG P for 0.95 Lag, 0.95 pu case. 'N/A' for solar. Source: PSS/E output.
46 | General | 0.95 Lagging, Voltage at POI 0.95 pu: WTG Q(pu) | p.u. | 0.95 | Q_WTG | 0.18 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG Q for 0.95 Lag, 0.95 pu case. 'N/A' for solar. Source: PSS/E output.
| General | Reactive Power Injection in pu(100MVA base) at PoI, 0.95 Lagging, Voltage at POI 1.0 pu | p.u. | 1 | Q_POI | 0.33 | -1.643 | 1.643 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Net reactive power injection at POI (p.u., 100 MVA base) for 0.95 Lagging PF, 1.0 pu voltage. Expected: ≈+0.3286 p.u. (≈328.6 MVAr for 1000 MW plant). Must meet CEA reactive power requirement.
| General | 0.95 Lagging, Voltage at POI 1.0 pu: Inverter P(pu) | p.u. | 1 | P_INV | 0.27 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter active power (p.u.) for 0.95 Lag, 1.0 pu case. Expected: ≈0.990 p.u. Source: PSS/E LF output.
| General | 0.95 Lagging, Voltage at POI 1.0 pu: Inverter Q(pu) | p.u. | 1 | Q_INV | 0.28 | -1 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter reactive power injection (p.u.) for 0.95 Lag case. Expected: ≈+0.329 p.u. Source: PSS/E LF output. Positive = capacitive (lagging current = leading reactive power injection).
| General | 0.95 Lagging, Voltage at POI 1.0 pu: SVG Q(pu) | p.u. | 1 | Q_SVG | 1 | -1 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | SVG reactive power for 0.95 Lag case. Enter actual value from PSS/E. May be 0 if SVG not dispatched. Source: PSS/E output.
| General | 0.95 Lagging, Voltage at POI 1.0 pu: WTG P(pu) | p.u. | 1 | P_WTG | 1 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG active power for 0.95 Lag case. Enter 'N/A' if pure solar. Source: PSS/E output.
| General | 0.95 Lagging, Voltage at POI 1.0 pu: WTG Q(pu) | p.u. | 1 | Q_WTG | 0.167 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG reactive power for 0.95 Lag case. Enter 'N/A' if pure solar. Source: PSS/E output.
47 | General | Reactive Power Injection in pu(100MVA base) at PoI, Unity pf , Voltage at POI 1.05 pu | p.u. | 1.05 | Q_POI | 0.02 | -1.643 | 0 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Net Q at POI for Unity PF, 1.05 pu voltage. Expected: ≈0.00 p.u. High voltage scenario – verify plant does not over-inject reactive power. Source: PSS/E output.
48 | General | Unity PF, Voltage at POI 1.05 pu: Inverter P(pu) | p.u. | 1.05 | P_INV | 0.26 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter P for Unity PF, 1.05 pu case. Source: PSS/E output.
49 | General | Unity PF, Voltage at POI 1.05 pu: Inverter Q(pu) | p.u. | 1.05 | Q_INV | 0 | -1 | 0 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter Q for Unity PF, 1.05 pu case. Should be ≈0. Source: PSS/E output.
51 | General | Unity PF, Voltage at POI 1.05 pu: SVG Q(pu) | p.u. | 1.05 | Q_SVG | 0.7 | -1 | 0 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | SVG Q for Unity PF, 1.05 pu case. Source: PSS/E output.
52 | General | Unity PF, Voltage at POI 1.05 pu: WTG P(pu) | p.u. | 1.05 | P_WTG | 1 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG P for Unity PF, 1.05 pu case. 'N/A' for solar. Source: PSS/E output.
53 | General | Unity PF, Voltage at POI 1.05 pu: WTG Q(pu) | p.u. | 1.05 | Q_WTG | 0 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG Q for Unity PF, 1.05 pu case. 'N/A' for solar. Source: PSS/E output.
54 | General | Reactive Power Injection in pu(100MVA base) at PoI, 0.95 leading , Voltage at POI 1.05 pu | p.u. | 1.05 | Q_POI | -0.33 | -1.643 | 0 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Net Q at POI for 0.95 Lead, 1.05 pu voltage. Expected: ≈−0.3286 p.u. This is the most demanding reactive absorption case. Source: PSS/E output.
55 | General | 0.95 Leading, Voltage at POI 1.05 pu: Inverter P(pu) | p.u. | 1.05 | P_INV | 0.27 | 0 | -1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter P for 0.95 Lead, 1.05 pu case. Source: PSS/E output.
56 | General | 0.95 Leading, Voltage at POI 1.05 pu: Inverter Q(pu) | p.u. | 1.05 | Q_INV | 0 | -1 | 0 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter Q for 0.95 Lead, 1.05 pu case. Should be ≈−0.329 p.u. (absorption). Source: PSS/E output.
58 | General | 0.95 Leading, Voltage at POI 1.05 pu: SVG Q(pu) | p.u. | 1.05 | Q_SVG | 0.02 | -1 | 0 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | SVG Q for 0.95 Lead, 1.05 pu case. Source: PSS/E output.
59 | General | 0.95 Leading, Voltage at POI 1.05 pu: WTG P(pu) | p.u. | 1.05 | P_WTG | 1 | 0 | -1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG P for 0.95 Lead, 1.05 pu case. 'N/A' for solar. Source: PSS/E output.
60 | General | 0.95 Leading, Voltage at POI 1.05 pu: WTG Q(pu) | p.u. | 1.05 | Q_WTG | 0 | 0 | -1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG Q for 0.95 Lead, 1.05 pu case. 'N/A' for solar. Source: PSS/E output.
26 | General | Reactive Power Injection in pu(100MVA base) at PoI, 0.95 Leading, Voltage at POI 1.0 pu | p.u. | 1 | Q_POI | -0.33 | -1.643 | 1.643 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Net reactive power at POI for 0.95 Leading PF, 1.0 pu case. Expected: ≈−0.3286 p.u. (absorption). Must demonstrate plant can absorb full reactive power requirement.
27 | General | 0.95 Leading, Voltage at POI 1.0 pu: Inverter P(pu) | p.u. | 1 | P_INV | 0.27 | 0 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter active power for 0.95 Lead case. Expected: ≈0.990 p.u. Source: PSS/E output.
28 | General | 0.95 Leading, Voltage at POI 1.0 pu: Inverter Q(pu) | p.u. | 1 | Q_INV | 0 | -1 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Inverter reactive power for 0.95 Lead case. Expected: ≈−0.329 p.u. (negative = absorption). Source: PSS/E output.
30 | General | 0.95 Leading, Voltage at POI 1.0 pu: SVG Q(pu) | p.u. | 1 | Q_SVG | 0 | -1 | 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | SVG reactive power for 0.95 Lead case. Source: PSS/E output.
31 | General | 0.95 Leading, Voltage at POI 1.0 pu: WTG P(pu) | p.u. | 1 | P_WTG | 1 | 0 | -1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG active power for 0.95 Lead case. 'N/A' for solar. Source: PSS/E output.
32 | General | 0.95 Leading, Voltage at POI 1.0 pu: WTG Q(pu) | p.u. | 1 | Q_WTG | 0 | 0 | -1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | WTG reactive power for 0.95 Lead case. 'N/A' for solar. Source: PSS/E output.
9 | General | Power Transformer Tap position | Tap-Position |  |  | Tap 1 | Tap 1 | Tap 1 | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 27 |  | Power transformer tap position used in PSS/E simulations. Must match physical tap setting. Typically 'Tap 1' = nominal. Preferred to remain constant across all scenarios unless otherwise justified.
10 | General | DTL configuration is as per intimation | Y/N |  |  | Yes | NA | NA | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 13 |  | Confirm DTL (Dedicated Transmission Line) configuration in PSS/E model matches CTU's intimation/connectivity approval. Enter 'Yes' or 'No'. Deviations are not allowed.
11 | General | Inverter P & Q operating points has been kept same | Y/N |  |  | Yes | NA | NA | 153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | 47 |  | Confirm inverter P and Q operating points are set identically for given scenario. Not the condition for compliance, but for the information. Enter 'Yes' or 'No'. Inconsistency causes comparison errors.
The Applicant is required to fill in yellow-highlighted cells only. All remaining fields are system-locked and pre-populated for reference.
Note on K21: Missing: - PSS/E LF Report.pdf
Note on K28: Missing: - PSS/E LF Report.pdf

## TD Requirement-RE
Technical Data Requirement for Renewable Sources
Sr. No. | Category | Description | Submission Status (Submitted) | Name of File/ Folder Name | Found? - Name of File/ Folder Name | Remarks on Files Found | Remarks | 📝 Developer Guidance / Explanatory Note
1 | Technical Details - IBR Unit | Technical Datasheet | Submitted | 3. Datasheets of all the equipment | Yes | Found | Submitted
2 | Technical Details - IBR Unit | Reactive Power Capability Curve (PQ, VQ curve) | Submitted | 8. IBR PQ Capability Curve 9. IBR Power Curve (Speed and Irradiance) | Yes | Found | Submitted
3 | Technical Details - IBR Unit | Temperature Derating PQ Curve | Submitted | 11. IBR Temperature Derating | Yes | Found | Submitted
4 | Technical Details - IBR Unit | Operator Manual of IBR unit(s) | Submitted | 12. Single Machines PSSE model and Benchmarking reports 13. Single Machines PSCAD model and Benchmarking reports | Yes | Found | Submitted
5 | Technical Details - IBR Unit | Proposed Protection Settings of IBR unit (in accordance with Grid-India's FTE&I procedure) | Submitted | 5. Controller and Protection Settings | Yes | Found | Submitted
6 | Technical Details - IBR Unit | Actual Protection Settings of IBR unit (in accordance with Grid-India's FTE&I procedure) | Submitted |  |  |  | Submitted
7 | Single Line Diagram | RE Pooling Station Switchyard (should include 220 kV, 33kV, IBR level SLD) | Submitted | 2. SLDs | Yes | Found | Submitted
8 | Single Line Diagram | Proposed Geographical SLD (shall comprise lengths, location of IBRs, conductor type, rating) | Submitted | H.4-Wind\H.4.4-Transmission Line\H.4.4.1-33kV Transmission Line Route Layout | Yes | Found | Submitted
9 | Equipment details | Technical Datasheet of IBR unit transformer (IDT) | Submitted | 3. Datasheets of all the equipment\H.3-Solar\H.3.4-Inverter Duty Transformer GA GTP | No | Missing: 3. Datasheets of all the equipment\H.3-Solar\H.3.4-Inverter Duty Transformer GA GTP | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
10 | Equipment details | Nameplate of the IBR unit transformer | Submitted | 3. Datasheets of all the equipment\H.4-Wind\H.4.2-WTG Transformer GA GTP & Schematics | No | Missing: 3. Datasheets of all the equipment\H.4-Wind\H.4.2-WTG Transformer GA GTP & Schematics | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
11 | Equipment details | Technical Datasheet of Power transformer | Submitted | 3. Datasheets of all the equipment\H.5-PSS\H.5.2-Power Transformer | Yes | Found | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
12 | Equipment details | Nameplate of the Power transformer | Submitted | 3. Datasheets of all the equipment\H.5-PSS\H.5.2-Power Transformer | Yes | Found | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
13 | Equipment details | Technical Datasheet of cables | Submitted | 3. Datasheets of all the equipment\H.3-Solar\H.3.5-CablesTD_Doc_013.pdf, 3. Datasheets of all the equipment\H.4-Wind\H.4.3-LT 3.3kV Cable GTP (WTG to USS Trafo) | No | Missing: 3. Datasheets of all the equipment\H.3-Solar\H.3.5-CablesTD_Doc_013.pdf | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
14 | Equipment details | Technical Datasheet of overhead conductors | Submitted | 3. Datasheets of all the equipment\H.3-Solar\H.3.6-Transmission Line\H.3.6.2-33kV Transmission Line Conductor GTP (Solar), 3. Datasheets of all the equipment\H.4-Wind\H.4.4-Transmission Line\Transmission Line Conductor GTP (Wind), 28. Miscellaneous\Annexure-A\Annexure-A.2-220kV Transmission line Conductor GTP, | Yes | Found | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
15 | Equipment details | Power Plant Controller (PPC)_MASTER | Submitted | 7. PPC PSCAD User manual | Yes | Found | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
16 | Equipment details | PPC Model & Make | Submitted |  |  |  | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
17 | Equipment details | Technical Datasheet of PPC | Submitted | 6. PPC Philosophy\EIT PPC Controller Datasheet | Yes | Found | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
18 | Equipment details | Functional description of the PPC and technical functionality document | Submitted | H.5-PSS\H.5.11-PPC | Yes | Found | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
19 | Equipment details | Operator manual of PPC | Submitted | H.5-PSS\H.5.11-PPC | Yes | Found | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
20 | Equipment details | Proposed protection setting and control mode of PPC | Submitted | 5. Controller and Protection Settings\4 PPC | Yes | Found | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
21 | Equipment details | Power Plant Controller (PPC)_SLAVE (if applicable) | Submitted | NA |  |  | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
22 | Equipment details | PPC Model & Make | Submitted | NA |  |  | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
23 | Equipment details | Technical Datasheet of PPC | Submitted | NA |  |  | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
24 | Equipment details | Functional description of the PPC and technical functionality document | Submitted | NA |  |  | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
25 | Equipment details | Operator manual of PPC | Submitted | NA |  |  | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
26 | Equipment details | Proposed protection setting and control mode of PPC | Submitted | NA |  |  | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
27 | Equipment details | Technical Details of SVG | Submitted | 3. Datasheets of all the equipment\H.5-PSS\H.5.1-SVG | Yes | Found | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
28 | Equipment details | Technical Datasheet of SVG | Submitted | 3. Datasheets of all the equipment\H.5-PSS\H.5.1-SVG | Yes | Found | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
29 | Equipment details | Control Philosophy document of SVG | Submitted | 12. Single Machines PSSE model and Benchmarking reports\3 SVG | Yes | Found | Submitted | Upload manufacturer-provided technical datasheets. Ensure documents are in English and cover ratings, performance curves, and protection settings.
30 | Equipment details | Operator Manual of the SVG | Submitted | 12. Single Machines PSSE model and Benchmarking reports\3 SVG | Yes | Found | Submitted | Upload manufacturer-provided Operational Manual. Ensure documents are in English and cover ratings, performance curves, and protection settings.
31 | Equipment details | Nameplate of SVG | Submitted | 3. Datasheets of all the equipment\H.5-PSS\H.5.1-SVG | Yes | Found | Submitted
32 | Equipment details | Line Length | Submitted | H.4-Wind\H.4.4-Transmission Line\H.4.4.1-33kV Transmission Line Route Layout | Yes | Found | Submitted
33 | Certification & Unit level testing to be furnished by the entity | Type Certification | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
34 | Certification & Unit level testing to be furnished by the entity | Type Certificate of single WTG Unit(s) | Submitted | 4. IBR EvaluationType Test Reports and SoC\2 WTG | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
35 | Certification & Unit level testing to be furnished by the entity | Type Test Report for Inverter / WTG (Tests to be covered as per CEA Connectivity Standards) | Submitted | 4. IBR EvaluationType Test Reports and SoC\2 WTG | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
36 | Certification & Unit level testing to be furnished by the entity | Harmonics | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
37 | Certification & Unit level testing to be furnished by the entity | DC Current Injection | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
38 | Certification & Unit level testing to be furnished by the entity | Flicker | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
39 | Certification & Unit level testing to be furnished by the entity | PQ Capability Test | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
40 | Certification & Unit level testing to be furnished by the entity | Capable to operate in frequency range: 47.5 Hz to 52 Hz with +/-5% voltage variation | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
41 | Certification & Unit level testing to be furnished by the entity | Capable to provide rated output in frequency range of 49.5 Hz to 50.5 Hz with +/-5% voltage variation | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
42 | Certification & Unit level testing to be furnished by the entity | LVRT (Shall include details of Id & Iq calculation principles for LVRT & HVRT) | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
43 | Certification & Unit level testing to be furnished by the entity | Active power control feature and Rate of change of active power | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
44 | Certification & Unit level testing to be furnished by the entity | Primary Frequency Response (PFR) | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
45 | Certification & Unit level testing to be furnished by the entity | Immediate (within 1 second) real power primary frequency response of at least 10% of the maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
46 | Certification & Unit level testing to be furnished by the entity | HVRT | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
47 | Certification & Unit level testing to be furnished by the entity | Evaluation Report on Test Reports of IBR Units | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
48 | Certification & Unit level testing to be furnished by the entity | Statement of Compliance of IBR Unit | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
49 | Certification & Unit level testing to be furnished by the entity | Test Reports for SVG/STATCOM Unit(s) - If installed | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
50 | Certification & Unit level testing to be furnished by the entity | Harmonics | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
51 | Certification & Unit level testing to be furnished by the entity | DC Current Injection | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
52 | Certification & Unit level testing to be furnished by the entity | Flicker | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
53 | Certification & Unit level testing to be furnished by the entity | PQ Capability Test | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
54 | Certification & Unit level testing to be furnished by the entity | Capable to operate in frequency range: 47.5 Hz to 52 Hz with +/-5% voltage variation | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
55 | Certification & Unit level testing to be furnished by the entity | Capable to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
56 | Certification & Unit level testing to be furnished by the entity | LVRT (Shall include details of Id & Iq calculation principles for LVRT & HVRT) | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
57 | Certification & Unit level testing to be furnished by the entity | HVRT | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
58 | Certification & Unit level testing to be furnished by the entity | Evaluation Report on Test Reports of SVG/STATCOM Unit(s) | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
59 | Certification & Unit level testing to be furnished by the entity | Statement of Compliance of SVG/STATCOM Unit(s) | Submitted | 4. IBR EvaluationType Test Reports and SoC | Yes | Found | Submitted | These are type test / certification reports from accredited labs. For each test, attach the full test report PDF.
60 | Unit Level Reports (Inverter) | Unit level technical datasheet ( including Irradiance Vs Power characteristics:Efficiency curve) | Submitted | 3. Datasheets of all the equipment\H.3-Solar\H.3.2-Inverter | Yes | Found | Submitted | OEM-provided unit-level model files and reports for the inverter/IBR.
61 | Unit Level Reports (Inverter) | Unit level Reactive power Capability curve alongwith temperature derating curve & QV curve | Submitted | 3. Datasheets of all the equipment\H.3-Solar\H.3.2-Inverter | Yes | Found | Submitted | OEM-provided unit-level model files and reports for the inverter/IBR.
62 | Unit Level Reports (Inverter) | Unit level Statement of Compliance (if applicable) | Submitted | 4. IBR EvaluationType Test Reports and SoC\1 Inverter | Yes | Found | Submitted
63 | Unit Level Reports (Inverter) | Unit level Evaluation report (if applicable) | Submitted | 4. IBR EvaluationType Test Reports and SoC\1 Inverter | Yes | Found | Submitted
64 | Unit Level Reports (Inverter) | Unit level Test report | Submitted | 4. IBR EvaluationType Test Reports and SoC\1 Inverter | Yes | Found | Submitted
65 | Unit Level Reports (Inverter) | Unit level PSCAD User manual | Submitted | 13. Single Machines PSCAD model and Benchmarking reports\1 Inverter | Yes | Found | Submitted
66 | Unit Level Reports (Inverter) | Operator Manual of IBR unit(s) | Submitted | 13. Single Machines PSCAD model and Benchmarking reports\1 Inverter | Yes | Found | Submitted
67 | Unit Level Reports (Inverter) | Unit level benchmarking report (PSS/E) | Submitted | 12. Single Machines PSSE model and Benchmarking reports\1 Inverter | Yes | Found | Submitted
68 | Unit Level Reports (Inverter) | Unit level benchmarking report (PSCAD) | Submitted | 13. Single Machines PSCAD model and Benchmarking reports\1 Inverter | Yes | Found | Submitted
69 | Unit Level Reports (Inverter) | Unit level comparison report (PSS/E,PSCAD & Test results) | Submitted | 13. Single Machines PSCAD model and Benchmarking reports\1 Inverter | Yes | Found | Submitted
70 | Unit Level Reports [SVG (if applicable)] | Technical datasheet | Submitted | 3. Datasheets of all the equipment\H.5-PSS\H.5.1-SVG | Yes | Found | Submitted
71 | Unit Level Reports [SVG (if applicable)] | PQ Capability curve alongwith derating curve | Submitted | 8. IBR PQ Capability Curve\3 SVG 11. IBR Temperature Derating\3 SVG | Yes | Found | Submitted
72 | Unit Level Reports [SVG (if applicable)] | Unit level Statement of Compliance (if applicable) | Submitted | 4. IBR EvaluationType Test Reports and SoC\3 SVG | Yes | Found | Submitted
73 | Unit Level Reports [SVG (if applicable)] | Unit level Evaluation report(if applicable) | Submitted | 4. IBR EvaluationType Test Reports and SoC\3 SVG | Yes | Found | Submitted
74 | Unit Level Reports [SVG (if applicable)] | Unit level Test report | Submitted | 4. IBR EvaluationType Test Reports and SoC\3 SVG | Yes | Found | Submitted
75 | Unit Level Reports [SVG (if applicable)] | Operator Manual of SVG unit(s) | Submitted | 12. Single Machines PSSE model and Benchmarking reports\3 SVG | Yes | Found | Submitted
76 | Unit Level Reports [SVG (if applicable)] | Unit level PSCAD User manual | Submitted | 13. Single Machines PSCAD model and Benchmarking reports\3 SVG | Yes | Found | Submitted
77 | Unit Level Reports [SVG (if applicable)] | Unit level benchmarking report (PSS/E) | Submitted | 12. Single Machines PSSE model and Benchmarking reports\3 SVG | Yes | Found | Submitted
78 | Unit Level Reports [SVG (if applicable)] | Unit level benchmarking report (PSCAD) | Submitted | 13. Single Machines PSCAD model and Benchmarking reports\3 SVG | Yes | Found | Submitted
79 | Unit Level Reports [SVG (if applicable)] | Unit level comparison report (PSS/E,PSCAD & Test results) | Submitted | 13. Single Machines PSCAD model and Benchmarking reports\3 SVG | Yes | Found | Submitted
80 | Unit Level Reports (WTG) | Unit level technical datasheet ( including Irradiance Vs Power characteristics:Efficiency curve) | Submitted | 3. Datasheets of all the equipment\H.4-Wind\H.4.1-WTG | Yes | Found | Submitted
81 | Unit Level Reports (WTG) | Unit level Reactive power Capability curve alongwith temperature derating curve & QV curve | Submitted | 8. IBR PQ Capability Curve\2 WTG, 9. IBR Power Curve (Speed and Irradiance)\2 WTG, 11. IBR Temperature Derating\2 WTG | Yes | Found | Submitted
82 | Unit Level Reports (WTG) | Unit level Statement of Compliance | Submitted | 4. IBR EvaluationType Test Reports and SoC\2 WTG | Yes | Found | Submitted
83 | Unit Level Reports (WTG) | Unit level Evaluation report | Submitted | 4. IBR EvaluationType Test Reports and SoC\2 WTG | Yes | Found | Submitted
84 | Unit Level Reports (WTG) | Unit level Test report | Submitted | 4. IBR EvaluationType Test Reports and SoC\2 WTG | Yes | Found | Submitted
85 | Unit Level Reports (WTG) | Operator Manual of WTG | Submitted | 12. Single Machines PSSE model and Benchmarking reports\2 WTG | Yes | Found | Submitted
86 | Unit Level Reports (WTG) | Unit level PSCAD User manual | Submitted | 13. Single Machines PSCAD model and Benchmarking reports\2 WTG | Yes | Found | Submitted
87 | Unit Level Reports (WTG) | Unit level benchmarking report (PSS/E) | Submitted | 12. Single Machines PSSE model and Benchmarking reports\2 WTG | Yes | Found | Submitted
88 | Unit Level Reports (WTG) | Unit level benchmarking report (PSCAD) | Submitted | 13. Single Machines PSCAD model and Benchmarking reports\2 WTG | Yes | Found | Submitted
89 | Unit Level Reports (WTG) | Unit level comparison report (PSS/E,PSCAD & Test results) | Submitted | 13. Single Machines PSCAD model and Benchmarking reports\2 WTG | Yes | Found | Submitted
90 | Unit Level Reports (BESS/PCS) (if applicable) | Unit level technical datasheet | Submitted | NA |  |  | Submitted
91 | Unit Level Reports (BESS/PCS) (if applicable) | Unit level Reactive power Capability curve alongwith temperature derating curve & QV curve | Submitted | NA |  |  | Submitted
92 | Unit Level Reports (BESS/PCS) (if applicable) | Unit level Statement of Compliance (if applicable) | Submitted | NA |  |  | Submitted
93 | Unit Level Reports (BESS/PCS) (if applicable) | Unit level Evaluation report (if applicable) | Submitted | NA |  |  | Submitted
94 | Unit Level Reports (BESS/PCS) (if applicable) | Unit level Test report | Submitted | NA |  |  | Submitted
95 | Unit Level Reports (BESS/PCS) (if applicable) | Operator Manual of BESS/PCS unit(s) | Submitted | NA |  |  | Submitted
96 | Unit Level Reports (BESS/PCS) (if applicable) | Unit level PSCAD User manual | Submitted | NA |  |  | Submitted
97 | Unit Level Reports (BESS/PCS) (if applicable) | Unit level benchmarking report (PSS/E) | Submitted | NA |  |  | Submitted
98 | Unit Level Reports (BESS/PCS) (if applicable) | Unit level benchmarking report (PSCAD) | Submitted | NA |  |  | Submitted
99 | Unit Level Reports (BESS/PCS) (if applicable) | Unit level comparison report (PSS/E, PSCAD & Test results) | Submitted | NA |  |  | Submitted
100 | PPC | PPC PSCAD user manual | Submitted | 7. PPC PSCAD User manual (master and slave (If any)) | Yes | Found | Submitted
101 | PPC | Plant specific PPC methodology | Submitted | 6. PPC Philosophy | Yes | Found | Submitted
102 | PPC | PPC Hardware-In-Loop Test Report (if available) | Submitted |  |  |  | Submitted
103 | Plant Level Study Reports | Steady State Simulation Report | Submitted | 15. PSSE Steady State Report\153.6 MW VEH Green_Hybrid_Koppal Steady State Study Report_V01.PDF | Yes | Found | Submitted
104 | Plant Level Study Reports | PSSE Dynamic Simulation Report | Submitted | 17. PSSE Dynamic Report\153.6 MW VEH Green_Hybrid_Koppal PSSE Model Study Report_V02.pdf | Yes | Found | Submitted
105 | Plant Level Study Reports | Power Quality Simulation Report | Submitted | 20. PSCAD Power Quality Report\Power_Quality_Report_VEH_Rev_B.pdf | Yes | Found | Submitted
106 | Plant Level Study Reports | PSCAD Dynamic Simulation Report | Submitted | 22. PSCAD Dynamic Report\VEH_153.6MW_PSCAD_DYNAMICS_REPORT_RevC.pdf | Yes | Found | Submitted
107 | Plant Level Study Reports | PSSE & PSCAD comparision Report | Submitted | 23. PSSE PSCAD Plant level Benchmarking Report\153.6 MW VEH Green_Hybrid_Koppal PSSE PSCAD Plant level Benchmarking Report_V01.pdf | Yes | Found | Submitted
108 | Plant Level RMS Files (PSS/E) | Steady State file name for detailed model (.SAV) : Voltage = 1.0 , 0.95 lag | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\1 PU\153.6 MW VEH_Hybrid_A3.sav | Yes | Found | Submitted
109 | Plant Level RMS Files (PSS/E) | Steady State file name for detailed model (.SAV) :Voltage = 0.95 , 0.95 lag | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\0.95 PU\153.6 MW VEH_Hybrid_B3.sav | Yes | Found | Submitted
110 | Plant Level RMS Files (PSS/E) | Steady State file name for detailed model (.SAV) :Voltage = 1.05, UPF | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\1.05 PU\153.6 MW VEH_Hybrid_C1.sav | Yes | Found | Submitted
111 | Plant Level RMS Files (PSS/E) | Steady State file name for detailed model (.SAV) :Voltage = 1.0, UPF | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\1 PU\153.6 MW VEH_Hybrid_A1.sav | Yes | Found | Submitted
112 | Plant Level RMS Files (PSS/E) | Steady State file name for detailed model (.SAV) :Voltage = 0.95, UPF | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\0.95 PU\153.6 MW VEH_Hybrid_B1.sav | Yes | Found | Submitted
113 | Plant Level RMS Files (PSS/E) | Steady State file name for detailed model (.SAV) :Voltage = 1.0 , 0.95 lead | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\1 PU\153.6 MW VEH_Hybrid_A4.sav | Yes | Found | Submitted
114 | Plant Level RMS Files (PSS/E) | Steady State file name for detailed model (.SAV) :Voltage = 1.05 , 0.95 lead | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\1.05 PU\153.6 MW VEH_Hybrid_C4.sav | Yes | Found | Submitted
115 | Plant Level RMS Files (PSS/E) | Steady State file name for aggregated model (.SAV) : Active Power=1.0pu,Voltage = 1.0 , 0.95 lag | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\1 PU\153.6 MW VEH_Hybrid_A3.sav | Yes | Found | Submitted
116 | Plant Level RMS Files (PSS/E) | Steady State file name for aggregated model (.SAV) : Active Power=1.0pu, Voltage = 1.0 , 0.95 lead | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\0.95 PU\153.6 MW VEH_Hybrid_B3.sav | Yes | Found | Submitted
117 | Plant Level RMS Files (PSS/E) | Steady State file name for aggregated model (.SAV) : Active Power=1.0pu, Voltage = 1.0, Q=UPF | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\1.05 PU\153.6 MW VEH_Hybrid_C1.sav | Yes | Found | Submitted
118 | Plant Level RMS Files (PSS/E) | Steady State file name for aggregated model (.SAV) : Active Power=0.9pu, Voltage = 1.0, Q=UPF | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\1 PU\153.6 MW VEH_Hybrid_A1.sav | Yes | Found | Submitted
119 | Plant Level RMS Files (PSS/E) | Steady State file name for aggregatedmodel (.SAV) : Active Power=0.5pu, Voltage = 1.0, Q=UPF | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\0.95 PU\153.6 MW VEH_Hybrid_B1.sav | Yes | Found | Submitted
120 | Plant Level RMS Files (PSS/E) | Steady State file name for aggregated model (.SAV) : Active Power=0.25pu, Voltage = 1.0, Q=UPF | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\1 PU\153.6 MW VEH_Hybrid_A4.sav | Yes | Found | Submitted
121 | Plant Level RMS Files (PSS/E) | Steady State file name for aggregated model (.SAV) : Active Power=0.10pu, Voltage = 1.0, Q=UPF | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\1.05 PU\153.6 MW VEH_Hybrid_C4.sav | Yes | Found | Submitted
122 | Plant Level RMS Files (PSS/E) | NCSFC for Short-Circuit analysis (.SEQ) -PSSE | Submitted | 14. PSSE Detailed Model\01 Hybrid\W SVG\1 PU\153.6 MW VEH_Hybrid_A3.sav | Yes | Found | Submitted
123 | Plant Level RMS Files (PSS/E) | Plant level dynamic file name for equivalent model(.DYR) - PSSE | Submitted | 17. PSSE Dynamic Report\05 PSSE DYR and OUT Files\153.6 MW VEH | Yes | Found | Submitted
124 | Plant Level EMT Models(PSCAD) | Power Quality files (.pscx/.pswx) - PSCAD | Submitted | 19. PSCAD Detailed Power Quality Model\with filter\withfilter.pswx | Yes | Found | Submitted
125 | Plant Level EMT Models(PSCAD) | Plant level detailed model for power quality studies (active power = 10%) - PSCAD | Submitted | 19. PSCAD Detailed Power Quality Model\with filter\10_153.6 MW VEH_Hybrid.pscx | Yes | Found | Submitted
126 | Plant Level EMT Models(PSCAD) | Plant level detailed model for power quality studies (active power = 20%) - PSCAD | Submitted | 19. PSCAD Detailed Power Quality Model\with filter\20_153.6 MW VEH_Hybrid.pscx | Yes | Found | Submitted
127 | Plant Level EMT Models(PSCAD) | Plant level detailed model for power quality studies (active power = 30%) - PSCAD | Submitted | 19. PSCAD Detailed Power Quality Model\with filter\30_153.6 MW VEH_Hybrid.pscx | Yes | Found | Submitted
128 | Plant Level EMT Models(PSCAD) | Plant level detailed model for power quality studies (active power = 40%) - PSCAD | Submitted | 19. PSCAD Detailed Power Quality Model\with filter\40_153.6 MW VEH_Hybrid.pscx | Yes | Found | Submitted
129 | Plant Level EMT Models(PSCAD) | Plant level detailed model for power quality studies (active power = 50%) - PSCAD | Submitted | 19. PSCAD Detailed Power Quality Model\with filter\50_153.6 MW VEH_Hybrid.pscx | Yes | Found | Submitted
130 | Plant Level EMT Models(PSCAD) | Plant level detailed model for power quality studies (active power = 60%) - PSCAD | Submitted | 19. PSCAD Detailed Power Quality Model\with filter\60_153.6 MW VEH_Hybrid.pscx | Yes | Found | Submitted
131 | Plant Level EMT Models(PSCAD) | Plant level detailed model for power quality studies (active power = 70%) - PSCAD | Submitted | 19. PSCAD Detailed Power Quality Model\with filter\70_153.6 MW VEH_Hybrid.pscx | Yes | Found | Submitted
132 | Plant Level EMT Models(PSCAD) | Plant level detailed model for power quality studies (active power = 80%) - PSCAD | Submitted | 19. PSCAD Detailed Power Quality Model\with filter\80_153.6 MW VEH_Hybrid.pscx | Yes | Found | Submitted
133 | Plant Level EMT Models(PSCAD) | Plant level detailed model for power quality studies (active power = 90%) - PSCAD | Submitted | 19. PSCAD Detailed Power Quality Model\with filter\90_153.6 MW VEH_Hybrid.pscx | Yes | Found | Submitted
134 | Plant Level EMT Models(PSCAD) | Plant level detailed model for power quality studies (active power = 100%) - PSCAD | Submitted | 19. PSCAD Detailed Power Quality Model\with filter\100_153.6 MW VEH_Hybrid.pscx | Yes | Found | Submitted
135 | Plant Level EMT Models(PSCAD) | Power Quality Harmonic Injection file/folder name (.txt) - PSCAD Requirement | Submitted | 19. PSCAD Detailed Power Quality Model\with filter | Yes | Found | Submitted
136 | Plant Level EMT Models(PSCAD) | Dynamic EMT model file name (.pscx/.pswx) - PSCAD | Submitted | 21. PSCAD Equivalent Model\VEH.pswx | Yes | Found | Submitted
137 | Plant Level EMT Models(PSCAD) | Resource folder name(s) as applicable for (.obj/.f/.lib etc) - PSCAD | Submitted | 21. PSCAD Equivalent Model\Resources | Yes | Found | Submitted
138 | Plant Level RMS Models(PSS/E) | Python files for RMS Simulation Batch Processing | Submitted | 17. PSSE Dynamic Report\Batch_Run_PSSE.py | Yes | Found | Submitted
139 | Plant Level EMT Models(PSCAD) | Python files for EMT Simulation Batch Processing | Submitted | 21. PSCAD Equivalent Model\VEH.pswx | Yes | Found | Submitted
The Applicant is required to fill in yellow-highlighted cells only. All remaining fields are system-locked and pre-populated for reference.
Note on F12: Missing: - 3. Datasheets of all the equipment\H.3-Solar\H.3.4-Inverter Duty Transformer GA GTP
Note on F13: Missing: - 3. Datasheets of all the equipment\H.4-Wind\H.4.2-WTG Transformer GA GTP & Schematics
Note on F16: Missing: - 3. Datasheets of all the equipment\H.3-Solar\H.3.5-CablesTD_Doc_013.pdf

## Power Quality
Power Quality Requirement for Renewable Energy Sources
Sl No | Category | Description | Harmonic Category | Unit | Value Observed | Limit | Ref Document-1 | Found? - Ref Document-1 | Remarks on Files Found | Page number of the document-Ref-1 | Remarks | 📝 Developer Guidance / Explanatory Note
1 | General | Short circuit level received input from CTU/RLDC | SCMVA_grid | MVA | 16893.53 | NA | 26. Technical note and explanations by developers & OEMs\Mail Ref_Actual shot circuit MVA of Koppal-II | Yes | Found | 1 | Short circuit data from CTU | Short Circuit Level (SCL) at POI in MVA. Obtain this value from CTU/RLDC via a formal letter or email. Do NOT estimate. Enter the value from CTU SCL communication.
2 | General | Thevenin Impedance Received from CTU/RLDC | Zgrid | Ohm | 2.865 | NA | 26. Technical note and explanations by developers & OEMs\Mail Ref_Actual shot circuit MVA of Koppal-II | Yes | Found | 1 | Short circuit data from CTU | Thevenin impedance at POI received from CTU/RLDC. Enter in complex form: 'R+jX Ohm'. Example: '3+4J'. Source: CTU SCL communication letter or email. Required for harmonic load flow setup.
3 | Harmonics | Harmonic current injections are as per test report (PSCAD model) |  | Y/N | Yes | NA | 20. PSCAD Power Quality Report\Power_Quality_Report_VEH_Rev_B | Yes | Found | 8 | PSCAD model harmonics within limits | Verify that harmonic current injections used in the PSCAD model match the type test report data for each 10% power bin. Enter 'Yes' if verified, 'No' if not. Attach Harmonic Study Report.
4 | Harmonics | Harmonic load flow achieved or solved |  | Y/N | Yes | NA | 20. PSCAD Power Quality Report\Power_Quality_Report_VEH_Rev_B | Yes | Found | 20 | Harmonic LF converged | Confirm the harmonic load flow simulation converged (solved). Enter 'Yes' if converged, 'No' if diverged. If 'No', revise model and re-run. Attach final converged study report.
5 | Harmonics | Unit level test report contain harmonic spectrum for each 10% active power bin |  | Y/N | Yes | NA | Type Test Report.pdf | No | Missing: Type Test Report.pdf | 22 | Spectra for each 10% power bin | Confirm the unit-level type test report contains harmonic spectrum (current THD at each harmonic order) for each 10% power bin from 10% to 100%. Enter 'Yes' or 'No'. Mandatory per CEA Connectivity Standards.
6 | Harmonics | Maximum Harmonic Current Distortion (TDD) | TDD (max) | % | 1.179 | 1.5% | 20. PSCAD Power Quality Report\Power_Quality_Report_VEH_Rev_B | Yes | Found | 29 | Below 1.5% limit ✓ | Enter the maximum Total Demand Distortion (TDD) value observed in harmonic load flow study as a percentage. Limit: ≤1.5%. Example: 1.1%. Source: PSCAD harmonic study report. Must be below limit.
7 | Harmonics | TDD- 2, 4, 6 : Maximum Observed Among All Cases | h = 2,4,6 | % | 0.3945% | 0.5% | 20. PSCAD Power Quality Report\Power_Quality_Report_VEH_Rev_B | Yes | Found | 32 | Below 0.5% limit ✓ | TDD for even harmonics (orders 2, 4, 6). Enter value in %. Limit: ≤0.5%. Source: Harmonic Study Report.
8 | Harmonics | TDD - 2≤h<11(except 2, 4 & 6) : Maximum Observed Among All Cases | 2< h <11 (except for 2,4,6) | % | 0.9431% | 1% | 20. PSCAD Power Quality Report\Power_Quality_Report_VEH_Rev_B | Yes | Found | 32 | Below 1.0% limit ✓ | TDD for harmonic orders 2 ≤ h < 11. Enter value in %. CEA Limit: ≤1.0%. Source: Harmonic Study Report. Example: 0.7%.
9 | Harmonics | TDD - 11≤h<17 : Maximum Observed Among All Cases | 11≤h<17 | % | 0.0735% | 0.5% | 20. PSCAD Power Quality Report\Power_Quality_Report_VEH_Rev_B | Yes | Found | 32 | Below 0.5% limit ✓ | TDD for harmonic orders 11 ≤ h < 17. Enter value in %. CEA Limit: ≤0.5%. Source: Harmonic Study Report. Example: 0.3%.
10 | Harmonics | TDD - 17≤h<23 : Maximum Observed Among All Cases | 17≤h<23 | % | 0.269% | 0.38% | 20. PSCAD Power Quality Report\Power_Quality_Report_VEH_Rev_B | Yes | Found | 32 | Below 0.38% limit ✓ | TDD for harmonic orders 17 ≤ h < 23. Enter value in %. CEA Limit: ≤0.38%. Source: Harmonic Study Report. Example: 0.22%.
11 | Harmonics | TDD - 23≤h<35 : Maximum Observed Among All Cases | 23≤h<35 | % | 0.0851% | 0.15% | 20. PSCAD Power Quality Report\Power_Quality_Report_VEH_Rev_B | Yes | Found | 32 | Below 0.1% limit ✓ | TDD for harmonic orders 23 ≤ h < 35. Enter value in %. CEA Limit: ≤0.15%. Source: Harmonic Study Report. Example: 0.06%.
12 | Harmonics | TDD - 35≤h<50 : Maximum Observed Among All Cases | 35≤h<50 | % | 0.00992% | 0.1% | 20. PSCAD Power Quality Report\Power_Quality_Report_VEH_Rev_B | Yes | Found | 32 | h>=35 band – no limit defined | TDD for harmonic orders 35 ≤ h < 50. Enter value in %. CEA Limit: ≤0.10%. Source: Harmonic Study Report. Typically very small (< 0.05%).
13 | DC Injection | DC Injection Current Observed : Maximum Observed Among All Cases | h = 0 (DC) | % | 0.024% | 0.5% | 20. PSCAD Power Quality Report\Power_Quality_Report_VEH_Rev_B | Yes | Found | 9 | Below 0.5% limit ✓ | DC Current Injection as a percentage of rated AC current at POI. CEA Limit: ≤0.5%. Verify from type test report or simulation. Example: 0.18%. Source: DC Injection Test Report.
14 | Flicker | Flicker - Short Term Limit | Flicker (St) | NA | 0.001 | 1% | 20. PSCAD Power Quality Report\Power_Quality_Report_VEH_Rev_B | Yes | Found | 11 | Pst = 0.52 ≤ 0.8 ✓ | Short-Term Flicker severity index (Pst) at POI. CEA Limit: Pst ≤ 1.0.Source: Flicker measurement or calculation/simulation report.
15 | Flicker | Flicker - Long Term Limit | Flicker (Lt) | NA | 0.001 | 0.8% | 20. PSCAD Power Quality Report\Power_Quality_Report_VEH_Rev_B | Yes | Found | 11 | Plt = 0.41 ≤ 0.6 ✓ | Long-Term Flicker severity index (Plt) at POI. CEA Limit: Plt ≤ 0.8. Typical value: 0.3–0.5. Source: Flicker test/simulation report.
16 | Voltage Unbalance | Voltage Unbalance as per IEC 61000-4-30 |  | % | 0.7 | 1.5 | Voltage Measurement Report.pdf | No | Missing: Voltage Measurement Report.pdf | 7 | ≤1% per IEC 61000-4-30 ✓ | Voltage Unbalance at POI measured per IEC 61000-4-30. CEA Limit: ≤1.5% (typically ≤1.0% per IEC). Enter measured/simulated value. Source: Power Quality measurement report.
17 | Harmonics | Inter-harmonic measurement data submitted (OPTIONAL) | h = 0.5,1.5,2.5,3.5,…. | Y/N | Submitted |  | Inter-harmonic Report | No | Missing: Inter-harmonic Report | 3 | Optional – voluntarily submitted | Optional submission. If inter-harmonic measurement data is available from type test, submit the report. Enter 'Submitted' if provided, or 'Not Submitted' if not measured. No mandatory limit.
The Applicant is required to fill in yellow-highlighted cells only. All remaining fields are system-locked and pre-populated for reference.
Note on I8: Missing: - Type Test Report.pdf
Note on I19: Missing: - Voltage Measurement Report.pdf
Note on I20: Missing: - Inter-harmonic Report

## Dynamic Data-RE
Dynamics Simulation Data for Renewable Energy Sources
Sl No | Category | Voltage Dip/Swell Depth | Description | Notation of Measured Electrical Quantities | Unit / Data Type | Value Observed (PSSE) | Value Observed (PSCAD) | Lower Limit(Mag) | Upper Limit(Mag) | Document Name | Found? - Document Name | Remarks on Files Found | Page number of the document | 📝 Developer Guidance / Explanatory Note | Visual Representation
1 | LVRT/HVRT |  | Is tripping of Inverter/WTG/PCS/SVG observed during in any LVRT/HVRT case? |  | Yes/No | No | No | NA | NA | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found |  | Dynamic check: Did any inverter/WTG/SVG trip (disconnect) during LVRT or HVRT simulation? Expected answer: 'No'. If 'Yes', identify the cause (protection settings, model error) and fix before submission.
2 | General/Unit Level |  | Are Id(direct-axis current) & Iq (quadrature-axis current) are as per equipment Fault Ride-Through(FRT) logic? |  | Yes/No | No | No | NA | NA | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found |  | Verify that Id (direct-axis current) and Iq (quadrature-axis current) responses in simulation match the FRT control logic specified in OEM firmware. Expected: 'Yes'. Source: PSSE & PSCAD Dynamics Report.
3 | General/Unit Level |  | Parameters as per Firmware/Benchmarking/Simulations are Aligned |  | Yes/No | No | No | NA | NA | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found |  | Confirm that model parameters (K-factor, time constants, thresholds) are consistent between firmware documentation, benchmarking reports, and simulation models (PSS/E and PSCAD). Expected: 'Yes'. Discrepancies must be resolved.
4 | LVRT/HVRT | V=15% | Incremental Reactive Current Injection of Inverter - Minimum among all aggregated inverters Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Del_Iq | p.u. | 0.10167 | 0.5898 | 0 |  | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 122 | Incremental Reactive Current injection (ΔIq in p.u.) by the inverter during 0.15 p.u. voltage dip (severe LVRT, 3-phase symmetrical fault), at 100% active power dispatch. Lower limit: >0.001 p.u. (must show reactive support). Source: PSS/E dynamics run, LVRT test case.
5 | LVRT/HVRT | V=15% | Total Reactive Current support - Minimum among all inverters Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Iq_f = Iq_pref + Del_Iq | p.u. | 0.33692 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 122 | Total reactive current at the inverter terminal during the 0.15 pu LVRT case. Addition of pre-fault current and incremental current.Enter minimum value amongst the all feeders/inverters.
6 | LVRT/HVRT | V=15% | Active Current of Inverter - Maximum among all inverters Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Id_INV_max | p.u. | 0.86964 | 0.2744 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 122 | Active current (Id in p.u.) of inverter during the same 0.15 pu LVRT case. Active current may reduces during LVRT to prioritize reactive support. Lower limit: >0.001. Source: PSS/E dynamics report.
7 | LVRT/HVRT | V=15% | Total Apparant Current of Inverter - Maximum among all inverters Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Irms_3PH_INV_max | p.u. | 0.93711 | 0.2747 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 122 | Total Apparant current (I in p.u.) of inverter during the same 0.15 pu LVRT case. Apparent current should be close to 1. Source: PSS/E dynamics report.
8 | LVRT/HVRT | V=15% | Active Power Recovery within 1 second of Fault Clearance Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ Solar | P_post_LVRT_1sec | % | 93.2 | 26.9% | 90 | 90 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 122 | % of pre-fault active power restored within 1 second of fault clearance (LVRT 0.15 pu, 100% P, symmetrical). CEA requirement: ≥90% recovery within 1 second. Source: PSS/E post-fault response curve.
9 | LVRT/HVRT | V=15% | Incremental Reactive Current Injection of WTG Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Del_Iq | p.u. | 1.0299 | 0.8673 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 124 | Incremental Reactive Current injection (ΔIq in p.u.) by the WTG during 0.15 p.u. voltage dip (severe LVRT, 3-phase symmetrical fault), at 100% active power dispatch. Lower limit: >0.001 p.u. (must show reactive support). Source: PSS/E dynamics run, LVRT test case.
10 | LVRT/HVRT | V=15% | Total Reactive Current support of WTG Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Iq_f = Iq_pref + Del_Iq | p.u. | 1.1 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 124 | Total reactive current at the WTG terminal during the 0.15 pu LVRT case. Addition of pre-fault current and incremental current.
11 | LVRT/HVRT | V=15% | Active Current of Inverter of WTG Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Id_WTG | p.u. | 1e-06 | 0.4418 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 124 | Active current (Id in p.u.) of WTG during the same 0.15 pu LVRT case. Active current may reduces during LVRT to prioritize reactive support. Lower limit: >0.001. Source: PSS/E dynamics report.
12 | LVRT/HVRT | V=15% | Total Apparant Current of WTG Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Irms_3PH_WTG | p.u. | 1.1 | 0.9427 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 124 | Total Apparant current (I in p.u.) of WTG during the same 0.15 pu LVRT case. Apparent current should be close to 1. Source: PSS/E & PSCAD dynamics report.
13 | LVRT/HVRT | V=15% | Active Power Recovery within 1 second of Fault Clearance Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ WTG | P_post_LVRT_1sec | % | 93.2 | 95.12% | 90 | 90 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 124 | % of pre-fault active power restored within 1 second of fault clearance (LVRT 0.15 pu, 100% P, symmetrical). CEA requirement: ≥90% recovery within 1 second. Source: PSS/E & PSCAD post-fault response curve.
14 | LVRT/HVRT | V=15% | Incremental Reactive Current Injection of SVG Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ SVG | Del_Iq | p.u. | 0.6 | 0.2915 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 123 | Incremental Reactive Current injection (ΔIq in p.u.) by the SVG during 0.15 p.u. voltage dip (severe LVRT, 3-phase symmetrical fault), at 100% active power dispatch. Lower limit: >0.001 p.u. (must show reactive support). Source: PSS/E dynamics run, LVRT test case.
15 | LVRT/HVRT | V=15% | Total Reactive Current support of SVG Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ SVG | Iq_f = Iq_pref + Del_Iq | p.u. | 0.5867 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 123 | Total reactive current at the SVG terminal during the 0.15 pu LVRT case. Addition of pre-fault current and incremental current.
16 | LVRT/HVRT | V=15% | Incremental Reactive Current Injection of PCS/BESS Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Del_Iq | p.u. | N.A | NA | 0 | 1 | N.A |  |  | N.A | Incremental Reactive Current injection (ΔIq in p.u.) by the PCS/BESS during 0.15 p.u. voltage dip (severe LVRT, 3-phase symmetrical fault), at 100% active power dispatch. Lower limit: >0.001 p.u. (must show reactive support). Source: PSS/E dynamics run, LVRT test case.
17 | LVRT/HVRT | V=15% | Total Reactive Current support of PCS/BESS Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Iq_f = Iq_pref + Del_Iq | p.u. | N.A | NA | -1 | 1 | N.A |  |  | N.A | Total reactive current at the PCS/BESS terminal during the 0.15 pu LVRT case. Addition of pre-fault current and incremental current.
18 | LVRT/HVRT | V=15% | Active Current of Inverter of PCS/BESS Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Id_PCS | p.u. | N.A | NA | 0.001 | 1 | N.A |  |  | N.A | Active current (Id in p.u.) of inverter during the same 0.15 pu LVRT case. Active current may reduces during LVRT to prioritize reactive support. Lower limit: >0.001. Source: PSS/E dynamics report.
19 | LVRT/HVRT | V=15% | Total Apparant Current of PCS/BESS Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Irms_3PH_PCS | p.u. | N.A | NA | 0.001 | 1 | N.A |  |  | N.A | Total Apparant current (I in p.u.) of Power Conversion System during the same 0.15 pu LVRT case. Apparent current should be close to 1. Source: PSS/E dynamics report.
20 | LVRT/HVRT | V=15% | Incremental Reactive Power Injection at Plant Voltage Dip 0.15 pu ¦ 100% P ¦ Symmetrical ¦ Plant | Del_Q | p.u. | 42.2946 | 0.12 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 121 | Incremental reactive power (MVAr) injected by the inverter during the 0.15 pu LVRT case. Proportional to voltage dip magnitude and K-factor. Should be positive and substantial. Source: PSS/E dynamics report.
21 | LVRT/HVRT | V=50% | Incremental Reactive Current Injection of Inverter - Minimum among all aggregated inverters Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Del_Iq | p.u. | 1.7551 | 0.3258 | 0 |  | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 118 | Incremental Reactive Current injection (ΔIq in p.u.) by the inverter during 0.50 p.u. voltage dip (severe LVRT, 3-phase symmetrical fault), at 100% active power dispatch. Lower limit: >0.001 p.u. (must show reactive support). Source: PSS/E dynamics run, LVRT test case.
22 | LVRT/HVRT | V=50% | Total Reactive Current support - Minimum among all inverters Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Iq_f = Iq_pref + Del_Iq | p.u. | 0.052422 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 118 | Total reactive current at the inverter terminal during the 0.50 pu LVRT case. Addition of pre-fault current and incremental current.Enter minimum value amongst the all feeders/inverters.
23 | LVRT/HVRT | V=50% | Active Current of Inverter - Maximum among all inverters Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Id_INV_max | p.u. | 0.28768 | 0.274 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 118 | Active current (Id in p.u.) of inverter during the same 0.50 pu LVRT case. Active current may reduces during LVRT to prioritize reactive support. Lower limit: >0.001. Source: PSS/E dynamics report.
24 | LVRT/HVRT | V=50% | Total Apparant Current of Inverter - Maximum among all inverters Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Irms_3PH_INV_max | p.u. | 0.54343 | 0.273 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 118 | Total Apparant current (I in p.u.) of inverter during the same 0.50 pu LVRT case. Apparent current should be close to 1. Source: PSS/E dynamics report.
25 | LVRT/HVRT | V=50% | Active Power Recovery within 1 second of Fault Clearance Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ Solar | P_post_LVRT_1sec | % | 0.6174 | 0.269 | 90 | 90 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 118 | % of pre-fault active power restored within 1 second of fault clearance (LVRT 0.50 pu, 100% P, symmetrical). CEA requirement: ≥90% recovery within 1 second. Source: PSS/E post-fault response curve.
26 | LVRT/HVRT | V=50% | Incremental Reactive Current Injection of WTG Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Del_Iq | p.u. | 4.92 | 0.4554 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 120 | Incremental Reactive Current injection (ΔIq in p.u.) by the WTG during 0.50 p.u. voltage dip (severe LVRT, 3-phase symmetrical fault), at 100% active power dispatch. Lower limit: >0.001 p.u. (must show reactive support). Source: PSS/E dynamics run, LVRT test case.
27 | LVRT/HVRT | V=50% | Total Reactive Current support of WTG Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Iq_f = Iq_pref + Del_Iq | p.u. | 0.6262 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 120 | Total reactive current at the WTG terminal during the 0.50 pu LVRT case. Addition of pre-fault current and incremental current.
28 | LVRT/HVRT | V=50% | Active Current of Inverter of WTG Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Id_WTG | p.u. | 0.68439 | 0.94 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 120 | Active current (Id in p.u.) of WTG during the same 0.50 pu LVRT case. Active current may reduces during LVRT to prioritize reactive support. Lower limit: >0.001. Source: PSS/E dynamics report.
29 | LVRT/HVRT | V=50% | Total Apparant Current of WTG Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Irms_3PH_WTG | p.u. | 0.84746 | 0.9384 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 120 | Total Apparant current (I in p.u.) of WTG during the same 0.50 pu LVRT case. Apparent current should be close to 1. Source: PSS/E & PSCAD dynamics report.
30 | LVRT/HVRT | V=50% | Active Power Recovery within 1 second of Fault Clearance Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ WTG | P_post_LVRT_1sec | % | 1.0987 | 95% | 90 | 90 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 120 | % of pre-fault active power restored within 1 second of fault clearance (LVRT 0.50 pu, 100% P, symmetrical). CEA requirement: ≥90% recovery within 1 second. Source: PSS/E & PSCAD post-fault response curve.
31 | LVRT/HVRT | V=50% | Incremental Reactive Current Injection of SVG Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ SVG | Del_Iq | p.u. | 67.4807 | 0.2919 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 119 | Incremental Reactive Current injection (ΔIq in p.u.) by the SVG during 0.50 p.u. voltage dip (severe LVRT, 3-phase symmetrical fault), at 100% active power dispatch. Lower limit: >0.001 p.u. (must show reactive support). Source: PSS/E dynamics run, LVRT test case.
32 | LVRT/HVRT | V=50% | Total Reactive Current support of SVG Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ SVG | Iq_f = Iq_pref + Del_Iq | p.u. | 0.5867 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 119 | Total reactive current at the SVG terminal during the 0.50 pu LVRT case. Addition of pre-fault current and incremental current.
33 | LVRT/HVRT | V=50% | Incremental Reactive Current Injection of PCS/BESS Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Del_Iq | p.u. | N.A | NA | 0 | 1 | N.A |  |  | N.A | Incremental Reactive Current injection (ΔIq in p.u.) by the PCS/BESS during 0.50 p.u. voltage dip (severe LVRT, 3-phase symmetrical fault), at 100% active power dispatch. Lower limit: >0.001 p.u. (must show reactive support). Source: PSS/E dynamics run, LVRT test case.
34 | LVRT/HVRT | V=50% | Total Reactive Current support of PCS/BESS Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Iq_f = Iq_pref + Del_Iq | p.u. | N.A | NA | -1 | 1 | N.A |  |  | N.A | Total reactive current at the PCS/BESS terminal during the 0.50 pu LVRT case. Addition of pre-fault current and incremental current.
35 | LVRT/HVRT | V=50% | Active Current of Inverter of PCS/BESS Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Id_PCS | p.u. | N.A | NA | 0.001 | 1 | N.A |  |  | N.A | Active current (Id in p.u.) of inverter during the same 0.50 pu LVRT case. Active current may reduces during LVRT to prioritize reactive support. Lower limit: >0.001. Source: PSS/E dynamics report.
36 | LVRT/HVRT | V=50% | Total Apparant Current of PCS/BESS Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Irms_3PH_PCS | p.u. | N.A | NA | 0.001 | 1 | N.A |  |  | N.A | Total Apparant current (I in p.u.) of Power Conversion System during the same 0.50 pu LVRT case. Apparent current should be close to 1. Source: PSS/E dynamics report.
37 | LVRT/HVRT | V=50% | Incremental Reactive Power Injection at Plant Voltage Dip 0.50 pu ¦ 100% P ¦ Symmetrical ¦ Plant | Del_Q | p.u. | 51.0141 | 0.346 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 117 | Incremental reactive power (MVAr) injected by the inverter during the 0.50 pu LVRT case. Proportional to voltage dip magnitude and K-factor. Should be positive and substantial. Source: PSS/E dynamics report.
38 | LVRT/HVRT | V=85% | Incremental Reactive Current Injection of Inverter - Minimum among all aggregated inverters Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Del_Iq | p.u. | 1.5298 | 0.0326 | 0 |  | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 114 | Incremental Reactive Current injection (ΔIq in p.u.) by the inverter during 0.85 p.u. voltage dip (severe LVRT, 3-phase symmetrical fault), at 100% active power dispatch. Lower limit: >0.001 p.u. (must show reactive support). Source: PSS/E dynamics run, LVRT test case.
39 | LVRT/HVRT | V=85% | Total Reactive Current support - Minimum among all inverters Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Iq_f = Iq_pref + Del_Iq | p.u. | 0.012269 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 114 | Total reactive current at the inverter terminal during the 0.85 pu LVRT case. Addition of pre-fault current and incremental current.Enter minimum value amongst the all feeders/inverters.
40 | LVRT/HVRT | V=85% | Active Current of Inverter - Maximum among all inverters Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Id_INV_max | p.u. | 0.24296 | 0.27 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 114 | Active current (Id in p.u.) of inverter during the same 0.85 pu LVRT case. Active current may reduces during LVRT to prioritize reactive support. Lower limit: >0.001. Source: PSS/E dynamics report.
41 | LVRT/HVRT | V=85% | Total Apparant Current of Inverter - Maximum among all inverters Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Irms_3PH_INV_max | p.u. | 0.27636 | 0.2733 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 114 | Total Apparant current (I in p.u.) of inverter during the same 0.85 pu LVRT case. Apparent current should be close to 1. Source: PSS/E dynamics report.
42 | LVRT/HVRT | V=85% | Active Power Recovery within 1 second of Fault Clearance Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ Solar | P_post_LVRT_1sec | % | 0.36975 | 0.2693 | 90 | 90 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 114 | % of pre-fault active power restored within 1 second of fault clearance (LVRT 0.85 pu, 100% P, symmetrical). CEA requirement: ≥90% recovery within 1 second. Source: PSS/E post-fault response curve.
43 | LVRT/HVRT | V=85% | Incremental Reactive Current Injection of WTG Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Del_Iq | p.u. | 4.9184 | 0.04 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 116 | Incremental Reactive Current injection (ΔIq in p.u.) by the WTG during 0.85 p.u. voltage dip (severe LVRT, 3-phase symmetrical fault), at 100% active power dispatch. Lower limit: >0.001 p.u. (must show reactive support). Source: PSS/E dynamics run, LVRT test case.
44 | LVRT/HVRT | V=85% | Total Reactive Current support of WTG Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Iq_f = Iq_pref + Del_Iq | p.u. | 0.24825 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 116 | Total reactive current at the WTG terminal during the 0.85 pu LVRT case. Addition of pre-fault current and incremental current.
45 | LVRT/HVRT | V=85% | Active Current of Inverter of WTG Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Id_WTG | p.u. | 0.31263 | 0.9484 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 116 | Active current (Id in p.u.) of WTG during the same 0.85 pu LVRT case. Active current may reduces during LVRT to prioritize reactive support. Lower limit: >0.001. Source: PSS/E dynamics report.
46 | LVRT/HVRT | V=85% | Total Apparant Current of WTG Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Irms_3PH_WTG | p.u. | 0.9613 | 0.9469 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 116 | Total Apparant current (I in p.u.) of WTG during the same 0.85 pu LVRT case. Apparent current should be close to 1. Source: PSS/E & PSCAD dynamics report.
47 | LVRT/HVRT | V=85% | Active Power Recovery within 1 second of Fault Clearance Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ WTG | P_post_LVRT_1sec | % | 1.0122 | 95.14% | 90 | 90 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 116 | % of pre-fault active power restored within 1 second of fault clearance (LVRT 0.85 pu, 100% P, symmetrical). CEA requirement: ≥90% recovery within 1 second. Source: PSS/E & PSCAD post-fault response curve.
48 | LVRT/HVRT | V=85% | Incremental Reactive Current Injection of SVG Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ SVG | Del_Iq | p.u. | 67.496 | 0.3 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 115 | Incremental Reactive Current injection (ΔIq in p.u.) by the SVG during 0.85 p.u. voltage dip (severe LVRT, 3-phase symmetrical fault), at 100% active power dispatch. Lower limit: >0.001 p.u. (must show reactive support). Source: PSS/E dynamics run, LVRT test case.
49 | LVRT/HVRT | V=85% | Total Reactive Current support of SVG Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ SVG | Iq_f = Iq_pref + Del_Iq | p.u. | 0.27495 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 115 | Total reactive current at the SVG terminal during the 0.85 pu LVRT case. Addition of pre-fault current and incremental current.
50 | LVRT/HVRT | V=85% | Incremental Reactive Current Injection of PCS/BESS Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Del_Iq | p.u. | NA | NA | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 10 | Incremental Reactive Current injection (ΔIq in p.u.) by the PCS/BESS during 0.85 p.u. voltage dip (severe LVRT, 3-phase symmetrical fault), at 100% active power dispatch. Lower limit: >0.001 p.u. (must show reactive support). Source: PSS/E dynamics run, LVRT test case.
51 | LVRT/HVRT | V=85% | Total Reactive Current support of PCS/BESS Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Iq_f = Iq_pref + Del_Iq | p.u. | NA | NA | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 11 | Total reactive current at the PCS/BESS terminal during the 0.85 pu LVRT case. Addition of pre-fault current and incremental current.
52 | LVRT/HVRT | V=85% | Active Current of Inverter of PCS/BESS Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Id_PCS | p.u. | NA | NA | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found |  | Active current (Id in p.u.) of inverter during the same 0.85 pu LVRT case. Active current may reduces during LVRT to prioritize reactive support. Lower limit: >0.001. Source: PSS/E dynamics report.
53 | LVRT/HVRT | V=85% | Total Apparant Current of PCS/BESS Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Irms_3PH_PCS | p.u. | NA | NA | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | NA | Total Apparant current (I in p.u.) of Power Conversion System during the same 0.85 pu LVRT case. Apparent current should be close to 1. Source: PSS/E dynamics report.
54 | LVRT/HVRT | V=85% | Incremental Reactive Power Injection at Plant Voltage Dip 0.85 pu ¦ 100% P ¦ Symmetrical ¦ Plant | Del_Q | p.u. | 37.798 | 0.1719 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 113 | Incremental reactive power (MVAr) injected by the inverter during the 0.85 pu LVRT case. Proportional to voltage dip magnitude and K-factor. Should be positive and substantial. Source: PSS/E dynamics report.
55 | LVRT/HVRT | V=15% | Incremental Positive Sequence Reactive Current Inverter Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ Solar | Del_Iq+ | p.u. | NA | -0.035 | 0 | 1 |  |  |  | 14 | PSCAD – Positive-sequence Incremental Reactive Current injection during 0.15 pu voltage dip caused by a Line-to-Line (LL) fault (asymmetric/unbalanced). Lower limit: >0.001. Typical: 0.4–0.6 p.u.
56 | LVRT/HVRT | V=15% | Negative Sequence Reactive Current Inverter Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ Solar | Iq- | p.u. | NA | -0.22 | -1 | 0 |  |  |  | 14 | PSS/E and PSCAD – Negative-sequence reactive current during 0.15 pu LL fault. Value is typically negative (absorption of negative sequence). Source: PSCAD dynamics report with unbalanced fault.
57 | LVRT/HVRT | V=15% | Active Current of WTG Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ WTG | Id_WTG | p.u. | NA | 0.35 | 0.001 | 1 |  |  |  |  | PSCAD – Active current at WTG terminals during 0.15 pu LL LVRT case. Source: PSCAD dynamics report.
58 | LVRT/HVRT | V=15% | Active Current of Inverter Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ Solar | Id_INV | p.u. | NA | 0.28 | 0 | 1 |  |  |  | 14 | PSCAD – Active current at Inverter terminals during 0.15 pu LL LVRT case. Source: PSCAD dynamics report.
59 | LVRT/HVRT | V=15% | Reactive Current of Inverter Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ Solar | Iq_f = Iq_pref + Del_Iq | p.u. | NA |  | -1 | 1 | PSSE Dynamics Report.pdf | Yes | Found | 11 | PSCAD– Reactive power support (MVAr) during 0.15 pu LL LVRT. Lower than symmetrical case. Source: PSCAD Dynamics Report.
60 | LVRT/HVRT | V=15% | Incremental Positive Sequence Reactive Current WTG Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ WTG | Del_Iq+ | p.u. | NA | 0.27 | 0 | 1 |  |  |  |  | PSCAD – Positive-sequence Incremental Reactive Current injection during 0.15 pu voltage dip caused by a Line-to-Line (LL) fault (asymmetric/unbalanced). Lower limit: >0.001. Typical: 0.4–0.6 p.u.
61 | LVRT/HVRT | V=15% | Negative Sequence Reactive Current WTG Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ WTG | Iq- | p.u. | NA | -0.53 | -1 | 0
62 | LVRT/HVRT | V=15% | Rective Current of SVG Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ SVG | Iq_f = Iq_pref + Del_Iq | p.u. | NA |  | -1 | 1 | PSSE Dynamics Report.pdf | Yes | Found | 11
63 | LVRT/HVRT | V=15% | Reactive Current of WTG Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ WTG | Iq_f = Iq_pref + Del_Iq | p.u. | NA |  | -1 | 1 | PSSE Dynamics Report.pdf | Yes | Found | 11
64 | LVRT/HVRT | V=15% | Incremental Positive Sequence Reactive Current PCS/BESS Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ PCS/BESS | Del_Iq+ | p.u. | NA | NA | 0 | 1 |  |  |  |  | PSCAD – Positive-sequence Incremental Reactive Current injection during 0.15 pu voltage dip caused by a Line-to-Line (LL) fault (asymmetric/unbalanced). Lower limit: >0.001. Typical: 0.4–0.6 p.u.
65 | LVRT/HVRT | V=15% | Negative Sequence Reactive Current PCS/BESS Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ PCS/BESS | Iq- | p.u. | NA | NA | -1 | 0
66 | LVRT/HVRT | V=15% | Active Current of PCS/BESS Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ PCS/BESS | Id_PCS | p.u. | NA | NA | 0.001 | 1 |  |  |  |  | PSCAD – Active current at PCS/BESS terminals during 0.15 pu LL LVRT case. Source: PSCAD dynamics report.
67 | LVRT/HVRT | V=15% | Reactive Current of PCS/BESS Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ PCS/BESS | Iq_f = Iq_pref + Del_Iq | p.u. | NA | NA | -1 | 1 | PSSE Dynamics Report.pdf | Yes | Found | 11
68 | LVRT/HVRT | V=15% | Incremental Positive Sequence Reactive Current SVG Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ SVG | Del_Iq+ | p.u. | NA | 1.095 | 0 | 1 |  |  |  |  | PSCAD – Positive-sequence Incremental Reactive Current injection during 0.15 pu voltage dip caused by a Line-to-Line (LL) fault (asymmetric/unbalanced). Lower limit: >0.001. Typical: 0.4–0.6 p.u.
69 | LVRT/HVRT | V=15% | Negative Sequence Reactive Current SVG Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ SVG | Iq- | p.u. | NA | 0.3096 | -1 | 0
70 | LVRT/HVRT | V=15% | Incremental Reactive Power Injection at Plant Voltage Dip 0.15 pu ¦ 100% P ¦ LL ¦ Plant | Del_Q | p.u. | 1 | 0.4613 | 0.001 | 1
71 | LVRT/HVRT | V=50% | Incremental Positive Sequence Reactive Current Inverter Voltage Dip 0.50 pu ¦ 100% P ¦ LL ¦ Solar | Del_Iq+ | p.u. | NA | -0.009 | 0 | 1 |  |  |  | 14 | PSCAD – Positive-sequence Incremental Reactive Current injection during 0.50 pu voltage dip caused by a Line-to-Line (LL) fault (asymmetric/unbalanced). Lower limit: >0.001. Typical: 0.4–0.6 p.u.
72 | LVRT/HVRT | V=50% | Negative Sequence Reactive Current Inverter Voltage Dip 0.50 pu ¦ 100% P ¦ LL ¦ Solar | Iq- | p.u. | NA | -0.11 | -1 | 0 |  |  |  | 14 | PSS/E and PSCAD – Negative-sequence reactive current during 0.50 pu LL fault. Value is typically negative (absorption of negative sequence). Source: PSCAD dynamics report with unbalanced fault.
73 | LVRT/HVRT | V=50% | Active Current of WTG Voltage Dip 0.50 pu ¦ 100% P ¦ LL ¦ WTG | Id_WTG | p.u. | NA | 0.798 | 0.001 | 1 |  |  |  |  | PSCAD – Active current at WTG terminals during 0.50 pu LL LVRT case. Source: PSCAD dynamics report.
74 | LVRT/HVRT | V=50% | Active Current of Inverter Voltage Dip 0.5 pu ¦ 100% P ¦ LL ¦ Solar | Id_INV | p.u. | NA | 0.29 | 0 | 1 |  |  |  |  | PSCAD – Active current at Inverter terminals during 0.50 pu LL LVRT case. Source: PSCAD dynamics report.
75 | LVRT/HVRT | V=50% | Reactive Current of Inverter Voltage Dip 0.5 pu ¦ 100% P ¦ LL ¦ Solar | Iq_f = Iq_pref + Del_Iq | p.u. | NA |  | -1 | 1 | PSSE Dynamics Report.pdf | Yes | Found | 11
76 | LVRT/HVRT | V=50% | Incremental Positive Sequence Reactive Current WTG Voltage Dip 0.5 pu ¦ 100% P ¦ LL ¦ WTG | Del_Iq+ | p.u. | NA | 0.2178 | 0 | 1 |  |  |  |  | PSCAD – Positive-sequence Incremental Reactive Current injection during 0.50 pu voltage dip caused by a Line-to-Line (LL) fault (asymmetric/unbalanced). Lower limit: >0.001. Typical: 0.4–0.6 p.u.
77 | LVRT/HVRT | V=50% | Negative Sequence Reactive Current WTG Voltage Dip 0.5 pu ¦ 100% P ¦ LL ¦ WTG | Iq- | p.u. | NA | -0.27 | -1 | 0
78 | LVRT/HVRT | V=50% | Reactive Current of SVG Voltage Dip 0.5 pu ¦ 100% P ¦ LL ¦ SVG | Iq_f = Iq_pref + Del_Iq | p.u. | NA |  | -1 | 1 | PSSE Dynamics Report.pdf | Yes | Found | 11
79 | LVRT/HVRT | V=50% | Reactive Current of WTG Voltage Dip 0.5 pu ¦ 100% P ¦ LL ¦ WTG | Iq_f = Iq_pref + Del_Iq | p.u. | NA |  | -1 | 1 | PSSE Dynamics Report.pdf | Yes | Found | 11
80 | LVRT/HVRT | V=50% | Incremental Positive Sequence Reactive Current PCS/BESS Voltage Dip 0.5 pu ¦ 100% P ¦ LL ¦ PCS/BESS | Del_Iq+ | p.u. | NA | NA | 0 | 1 |  |  |  |  | PSCAD – Positive-sequence Incremental Reactive Current injection during 0.50 pu voltage dip caused by a Line-to-Line (LL) fault (asymmetric/unbalanced). Lower limit: >0.001. Typical: 0.4–0.6 p.u.
81 | LVRT/HVRT | V=50% | Negative Sequence Reactive Current PCS/BESS Voltage Dip 0.5 pu ¦ 100% P ¦ LL ¦ PCS/BESS | Iq- | p.u. | NA | NA | -1 | 0
82 | LVRT/HVRT | V=50% | Active Current of PCS/BESS Voltage Dip 0.5 pu ¦ 100% P ¦ LL ¦ PCS/BESS | Id_PCS | p.u. | NA | NA | 0.001 | 1 |  |  |  |  | PSCAD – Active current at PCS/BESS terminals during 0.50 pu LL LVRT case. Source: PSCAD dynamics report.
83 | LVRT/HVRT | V=50% | Reactive Current of PCS/BESS Voltage Dip 0.5 pu ¦ 100% P ¦ LL ¦ PCS/BESS | Iq_f = Iq_pref + Del_Iq | p.u. | NA | NA | -1 | 1 | PSSE Dynamics Report.pdf | Yes | Found | 11
84 | LVRT/HVRT | V=50% | Incremental Positive Sequence Reactive Current SVG Voltage Dip 0.5 pu ¦ 100% P ¦ LL ¦ SVG | Del_Iq+ | p.u. | NA | 0.292 | 0 | 1 |  |  |  |  | PSCAD – Positive-sequence Incremental Reactive Current injection during 0.50 pu voltage dip caused by a Line-to-Line (LL) fault (asymmetric/unbalanced). Lower limit: >0.001. Typical: 0.4–0.6 p.u.
85 | LVRT/HVRT | V=50% | Negative Sequence Reactive Current SVG Voltage Dip 0.5 pu ¦ 100% P ¦ LL ¦ SVG | Iq- | p.u. | NA | 0.121 | -1 | 0
86 | LVRT/HVRT | V=50% | Incremental Reactive Power Injection at Plant Voltage Dip 0.5 pu ¦ 100% P ¦ LL ¦ Plant | Del_Q | p.u. | 1 | 0.287 | 0.001 | 1
87 | LVRT/HVRT | V=85% | Incremental Positive Sequence Reactive Current Inverter Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ Solar | Del_Iq+ | p.u. | NA | 0.2914 | 0 | 1 |  |  |  | 14 | PSCAD – Positive-sequence Incremental Reactive Current injection during 0.85 pu voltage dip caused by a Line-to-Line (LL) fault (asymmetric/unbalanced). Lower limit: >0.001. Typical: 0.4–0.6 p.u.
88 | LVRT/HVRT | V=85% | Negative Sequence Reactive Current Inverter Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ Solar | Iq- | p.u. | NA |  | -1 | 0 |  |  |  | 14 | PSS/E and PSCAD – Negative-sequence reactive current during 0.85 pu LL fault. Value is typically negative (absorption of negative sequence). Source: PSCAD dynamics report with unbalanced fault.
89 | LVRT/HVRT | V=85% | Active Current of WTG Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ WTG | Id_WTG | p.u. | NA | 1 | 0.001 | 1 |  |  |  |  | PSCAD – Active current at WTG terminals during 0.85 pu LL LVRT case. Source: PSCAD dynamics report.
90 | LVRT/HVRT | V=85% | Active Current of Inverter Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ Solar | Id_INV | p.u. | NA | 0.28 | 0 | 1 |  |  |  |  | PSCAD – Active current at Inverter terminals during 0.85 pu LL LVRT case. Source: PSCAD dynamics report.
91 | LVRT/HVRT | V=85% | Reactive Current of Inverter Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ Solar | Iq_f = Iq_pref + Del_Iq | p.u. | NA |  | -1 | 1 | PSSE Dynamics Report.pdf | Yes | Found | 11
92 | LVRT/HVRT | V=85% | Incremental Positive Sequence Reactive Current WTG Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ WTG | Del_Iq+ | p.u. | NA | 0 | 0 | 1 |  |  |  |  | PSCAD – Positive-sequence Incremental Reactive Current injection during 0.85 pu voltage dip caused by a Line-to-Line (LL) fault (asymmetric/unbalanced). Lower limit: >0.001. Typical: 0.4–0.6 p.u.
93 | LVRT/HVRT | V=85% | Negative Sequence Reactive Current WTG Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ WTG | Iq- | p.u. | NA | -0.027 | -1 | 0
94 | LVRT/HVRT | V=85% | Reactive Current of SVG Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ SVG | Iq_f = Iq_pref + Del_Iq | p.u. | NA |  | -1 | 1 | PSSE Dynamics Report.pdf | Yes | Found | 11
95 | LVRT/HVRT | V=85% | Reactive Current of WTG Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ WTG | Iq_f = Iq_pref + Del_Iq | p.u. | NA |  | -1 | 1 | PSSE Dynamics Report.pdf | Yes | Found | 11
96 | LVRT/HVRT | V=85% | Incremental Positive Sequence Reactive Current PCS/BESS Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ PCS/BESS | Del_Iq+ | p.u. | NA | NA | 0 | 1 |  |  |  |  | PSCAD – Positive-sequence Incremental Reactive Current injection during 0.85 pu voltage dip caused by a Line-to-Line (LL) fault (asymmetric/unbalanced). Lower limit: >0.001. Typical: 0.4–0.6 p.u.
97 | LVRT/HVRT | V=85% | Negative Sequence Reactive Current PCS/BESS Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ PCS/BESS | Iq- | p.u. | NA | NA | -1 | 0
98 | LVRT/HVRT | V=85% | Active Current of PCS/BESS Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ PCS/BESS | Id_PCS | p.u. | NA | NA | 0.001 | 1 |  |  |  |  | PSCAD – Active current at PCS/BESS terminals during 0.85 pu LL LVRT case. Source: PSCAD dynamics report.
99 | LVRT/HVRT | V=85% | Reactive Current of PCS/BESS Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ PCS/BESS | Iq_f = Iq_pref + Del_Iq | p.u. | NA | NA | -1 | 1 | PSSE Dynamics Report.pdf | Yes | Found | 11
100 | LVRT/HVRT | V=85% | Incremental Positive Sequence Reactive Current SVG Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ SVG | Del_Iq+ | p.u. | NA | 0.3 | 0 | 1 |  |  |  |  | PSCAD – Positive-sequence Incremental Reactive Current injection during 0.85 pu voltage dip caused by a Line-to-Line (LL) fault (asymmetric/unbalanced). Lower limit: >0.001. Typical: 0.4–0.6 p.u.
101 | LVRT/HVRT | V=85% | Negative Sequence Reactive Current SVG Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ SVG | Iq- | p.u. | NA | 0.04 | -1 | 0
102 | LVRT/HVRT | V=85% | Incremental Reactive Power Injection at Plant Voltage Dip 0.85 pu ¦ 100% P ¦ LL ¦ Plant | Del_Q | p.u. | 1 | 0.1 | 0.001 | 1
103 | LVRT/HVRT | V=110% | Incremental Reactive Current of Inverter HVRT 1.1 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Del_Iq | p.u. | -0.005364 | 0.0018 | -1 | 0 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 201 | Incremental Reactive Current absorbed by inverter during HVRT 1.1 pu case (100% P, symmetrical). During HVRT, inverter absorbs reactive power (negative ΔIq). Lower limit: >0.0001.
104 | LVRT/HVRT | V=110% | Total Reactive Current of Inverter HVRT 1.1 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Iq_f = Iq_pref + Del_Iq | p.u. | 0.23118 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 201
105 | LVRT/HVRT | V=110% | Active Current of Inverter HVRT 1.1 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Id_INV | p.u. | 0.027965 | 0.267 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 201 | Active current maintained at Inverter terminals during HVRT 1.1 pu case. Should remain close to 1.0 p.u. Source: PSS/E dynamics output.
106 | LVRT/HVRT | V=110% | Incremental Reactive Current of WTG HVRT 1.1 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Del_Iq | p.u. | -0.11778 | 0.0524 | -1 | 0 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 202 | Incremental Reactive Current absorbed by WTG during HVRT 1.1 pu case (100% P, symmetrical). During HVRT, inverter absorbs reactive power (negative ΔIq). Lower limit: >0.0001.
107 | LVRT/HVRT | V=110% | Total Reactive Current of WTG HVRT 1.1 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Iq_f = Iq_pref + Del_Iq | p.u. | -0.11769 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 202
108 | LVRT/HVRT | V=110% | Active Current of WTG HVRT 1.1 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Id_WTG | p.u. | 0.93915 | 0.0688 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 202 | Active current maintained at WTG terminals during HVRT 1.1 pu case. Should remain close to 1.0 p.u. Source: PSS/E dynamics output.
109 | LVRT/HVRT | V=110% | Incremental Reactive Current of PCS/BESS HVRT 1.1 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Del_Iq | p.u. | NA | NA | -1 | 0 | NA |  |  | NA | Incremental Reactive Current absorbed by PCS/BESS during HVRT 1.1 pu case (100% P, symmetrical). During HVRT, inverter absorbs reactive power (negative ΔIq). Lower limit: >0.0001.
110 | LVRT/HVRT | V=110% | Total Reactive Current of PCS/BESS HVRT 1.1 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Iq_f = Iq_pref + Del_Iq | p.u. | NA | NA | -1 | 1 | NA |  |  | NA
111 | LVRT/HVRT | V=110% | Active Current of PCS/BESS HVRT 1.1 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Id_PCS | p.u. | NA | NA | 0.001 | 1 | NA |  |  | NA | Active current maintained at PCS/BESS terminals during HVRT 1.1 pu case. Should remain close to 1.0 p.u. Source: PSS/E dynamics output.
112 | LVRT/HVRT | V=110% | Incremental Reactive Current of SVG HVRT 1.1 pu ¦ 100% P ¦ Symmetrical ¦ SVG | Del_Iq | p.u. | -0.12723 | 0.8483 | -1 | 0 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 203 | Incremental Reactive Current absorbed by SVG during HVRT 1.1 pu case (100% P, symmetrical). During HVRT, inverter absorbs reactive power (negative ΔIq). Lower limit: >0.0001.
113 | LVRT/HVRT | V=110% | Total Reactive Current of SVG HVRT 1.1 pu ¦ 100% P ¦ Symmetrical ¦ SVG | Iq_f = Iq_pref + Del_Iq | p.u. | 0.62216 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 203
114 | LVRT/HVRT | V=120% | Incremental Reactive Current of Inverter HVRT 1.2 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Del_Iq | p.u. | -0.00019 | 0.0007 | -1 | 0 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 198 | Incremental Reactive Current absorbed by inverter during HVRT 1.2 pu case (100% P, symmetrical). During HVRT, inverter absorbs reactive power (negative ΔIq). Lower limit: >0.0001.
115 | LVRT/HVRT | V=120% | Total Reactive Current of Inverter HVRT 1.2 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Iq_f = Iq_pref + Del_Iq | p.u. | 0.22801 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 198
116 | LVRT/HVRT | V=120% | Active Currentof Inverter HVRT 1.2 pu ¦ 100% P ¦ Symmetrical ¦ Solar | Id_INV | p.u. | 0.43526 | 0.24 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 198 | Active current maintained at Inverter terminals during HVRT 1.2 pu case. Should remain close to 1.0 p.u. Source: PSS/E dynamics output.
117 | LVRT/HVRT | V=120% | Incremental Reactive Current of WTG HVRT 1.2 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Del_Iq | p.u. | 0.000633 | 0.0273 | -1 | 0 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 200 | Incremental Reactive Current absorbed by WTG during HVRT 1.2 pu case (100% P, symmetrical). During HVRT, inverter absorbs reactive power (negative ΔIq). Lower limit: >0.0001.
118 | LVRT/HVRT | V=120% | Total Reactive Current of WTG HVRT 1.2 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Iq_f = Iq_pref + Del_Iq | p.u. | 0.15473 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 200
119 | LVRT/HVRT | V=120% | Active Current of WTG HVRT 1.2 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Id_WTG | p.u. | 0.95755 | 0.854 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 200 | Active current maintained at WTG terminals during HVRT 1.2 pu case. Should remain close to 1.0 p.u. Source: PSS/E dynamics output.
120 | LVRT/HVRT | V=120% | Incremental Reactive Current of BESS/PCS HVRT 1.2 pu ¦ 100% P ¦ Symmetrical ¦ BESS/PCS | Del_Iq | p.u. | NA | NA | -1 | 0 | NA |  |  | NA | Incremental Reactive Current absorbed by PCS/BESS during HVRT 1.2 pu case (100% P, symmetrical). During HVRT, inverter absorbs reactive power (negative ΔIq). Lower limit: >0.0001.
121 | LVRT/HVRT | V=120% | Total Reactive Current of BESS/PCS HVRT 1.2 pu ¦ 100% P ¦ Symmetrical ¦ BESS/PCS | Iq_f = Iq_pref + Del_Iq | p.u. | NA | NA | -1 | 1 | NA |  |  | NA
122 | LVRT/HVRT | V=120% | Active Current of BESS/PCS HVRT 1.2 pu ¦ 100% P ¦ Symmetrical ¦ BESS/PCS | Id_PCS | p.u. | NA | NA | 0.001 | 1 | NA |  |  | NA | Active current maintained at PCS/BESS terminals during HVRT 1.2 pu case. Should remain close to 1.0 p.u. Source: PSS/E dynamics output.
123 | LVRT/HVRT | V=120% | Incremental Reactive Current of SVG HVRT 1.2 pu ¦ 100% P ¦ Symmetrical ¦ SVG | Del_Iq | p.u. | 0.001025 | 1.045 | -1 | 0 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 199 | Incremental Reactive Current absorbed by SVG during HVRT 1.2 pu case (100% P, symmetrical). During HVRT, inverter absorbs reactive power (negative ΔIq). Lower limit: >0.0001.
124 | LVRT/HVRT | V=120% | Total Reactive Current of SVG HVRT 1.2 pu ¦ 100% P ¦ Symmetrical ¦ SVG | Iq_f = Iq_pref + Del_Iq | p.u. | -0.076953 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 199
125 | LVRT/HVRT | V=120% | Incremental Reactive Power absorption at plant at POI HVRT 1.2 pu ¦ 100% P ¦ Symmetrical ¦ plant | Del_Q | p.u. | 0.2906 | -0.42 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 197
126 | LVRT/HVRT | V=120% | Total Reactive Power absorption at plant at POI HVRT 1.2 pu ¦ 100% P ¦ Symmetrical ¦ plant | Del_Q | p.u. | 1.0119 | 0.72 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 197
127 | LVRT/HVRT | V=130% | Incremental Reactive Current of Inverter HVRT 1.3 pu ¦ 100% P ¦ Symmetrical | Del_Iq | p.u. | -0.021493 | 0.0368 | -1 | 0 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 194 | Incremental Reactive Current absorbed by inverter during HVRT 1.3 pu case (100% P, symmetrical). During HVRT, inverter absorbs reactive power (negative ΔIq). Lower limit: >0.0001.
128 | LVRT/HVRT | V=130% | Total Reactive Current of Inverter HVRT 1.3 pu ¦ 100% P ¦ Symmetrical | Iq_f = Iq_pref + Del_Iq | p.u. | 0.21503 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 194 | Active current during HVRT 1.3 pu. May reduce due to current limit. Source: PSS/E report.
129 | LVRT/HVRT | V=130% | Active Currentof Inverter HVRT 1.3 pu ¦ 100% P ¦ Symmetrical | Id_INV | p.u. | -0.097073 | 0.249 | 0 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 194 | Active current maintained at Inverter terminals during HVRT 1.3 pu case. Should remain close to 1.0 p.u. Source: PSS/E dynamics output.
130 | LVRT/HVRT | V=130% | Incremental Reactive Current of WTG HVRT 1.3 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Del_Iq | p.u. | -0.34123 | -0.08582 | -1 | 0 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 196 | Incremental Reactive Current absorbed by WTG during HVRT 1.3 pu case (100% P, symmetrical). During HVRT, inverter absorbs reactive power (negative ΔIq). Lower limit: >0.0001.
131 | LVRT/HVRT | V=130% | Total Reactive Current of WTG HVRT 1.3 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Iq_f = Iq_pref + Del_Iq | p.u. | -0.34115 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 196 | Active current during HVRT 1.3 pu. May reduce due to current limit. Source: PSS/E report.
132 | LVRT/HVRT | V=130% | Active Currentof WTG HVRT 1.3 pu ¦ 100% P ¦ Symmetrical ¦ WTG | Id_WTG | p.u. | 0.82678 | 0.8708 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 196 | Active current maintained at WTG terminals during HVRT 1.3 pu case. Should remain close to 1.0 p.u. Source: PSS/E dynamics output.
133 | LVRT/HVRT | V=130% | Incremental Reactive Current of PCS/BESS HVRT 1.3 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Del_Iq | p.u. | NA | NA | -1 | 0 |  |  |  | NA | Incremental Reactive Current absorbed by PCS/BESS during HVRT 1.3 pu case (100% P, symmetrical). During HVRT, inverter absorbs reactive power (negative ΔIq). Lower limit: >0.0001.
134 | LVRT/HVRT | V=130% | Total Reactive Current of PCS/BESS HVRT 1.3 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Iq_f = Iq_pref + Del_Iq | p.u. | NA | NA | -1 | 1 |  |  |  | NA | Active current during HVRT 1.3 pu. May reduce due to current limit. Source: PSS/E report.
135 | LVRT/HVRT | V=130% | Active Currentof Inverter of PCS/BESS HVRT 1.3 pu ¦ 100% P ¦ Symmetrical ¦ PCS/BESS | Id_PCS | p.u. | NA | NA | 0.001 | 1 |  |  |  | NA | Active current maintained at PCS/BESS terminals during HVRT 1.3 pu case. Should remain close to 1.0 p.u. Source: PSS/E dynamics output.
136 | LVRT/HVRT | V=130% | Incremental Reactive Current of SVG HVRT 1.3 pu ¦ 100% P ¦ Symmetrical ¦ SVG | Del_Iq | p.u. | -0.50698 | 1.0475 | -1 | 0 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 195 | Incremental Reactive Current absorbed by SVG during HVRT 1.3 pu case (100% P, symmetrical). During HVRT, inverter absorbs reactive power (negative ΔIq). Lower limit: >0.0001.
137 | LVRT/HVRT | V=130% | Total Reactive Current of SVG HVRT 1.3 pu ¦ 100% P ¦ Symmetrical ¦ SVG | Iq_f = Iq_pref + Del_Iq | p.u. | 0.24178 |  | -1 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 195 | Active current during HVRT 1.3 pu. May reduce due to current limit. Source: PSS/E report.
138 | LVRT/HVRT | V=130% | Incremental Reactive Power aboroption at plant HVRT 1.3 pu ¦ 100% P ¦ Symmetrical ¦ Plant | Del_Q | p.u. | -89.4722 | -0.6862 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 193 | Active current during HVRT 1.3 pu. May reduce due to current limit. Source: PSS/E report.
139 | LVRT/HVRT | V=130% | Total Reactive Power aboroption at plant HVRT 1.3 pu ¦ 100% P ¦ Symmetrical ¦ Plant | Del_Q | p.u. | 0.87112 | 0.99 | 0.001 | 1 | Annexure PSSE Model Study Response for Hybrid Operation.pdf | Yes | Found | 193 | Active current during HVRT 1.3 pu. May reduce due to current limit. Source: PSS/E report.
140 | LVRT/HVRT |  | Does Master/Slave PPC freeze occur for all the cases |  | Yes/No | No | Yes | NA | NA | PSSE LVRT Report | Yes | Found | 32 | Confirm that the Master/Slave PPC does NOT freeze (halt commands) during any LVRT/HVRT case. Expected: 'No' freeze. If 'Yes', review PPC LVRT mode logic and fix. Source: PSS/E LVRT report.
141 | LVRT/HVRT |  | Master PPC LVRT Threshold voltage setting |  | p.u. | 0.85 | 0.9 | NA | NA | PSSE LVRT Report | Yes | Found | 33 | Voltage threshold (p.u.) at which Master PPC enters LVRT mode. Typical setting: 0.85 p.u. Must match firmware setting and CTU requirements. Source: PPC firmware documentation.
142 | LVRT/HVRT |  | Slave PPC LVRT Threshold voltage setting (if available) |  | p.u. | 0.75 | NA | NA | NA | PSSE LVRT Report | Yes | Found | 33 | Voltage threshold (p.u.) for Slave PPC LVRT activation (if Slave PPC exists). Typically slightly lower than Master (e.g., 0.75 p.u.). Enter 'N/A' if no Slave PPC.
143 | LVRT/HVRT |  | Hysteresis of Inverter kept for LVRT activation de-activation |  | Number | 3 | 0.06 | 0 | 0 | PSSE LVRT Report | Yes | Found | 34 | Hysteresis cycles (count) for LVRT mode activation/deactivation logic in inverter firmware. Prevents rapid chattering near threshold. Typical value: 2–5 cycles. Source: Inverter firmware doc.
144 | LVRT/HVRT |  | Hysteresis of SVG kept for LVRT activation de-activation |  | Number | 5 | 0.05 | 0 | 0 | PSSE LVRT Report | Yes | Found | 35 | Hysteresis cycles for SVG LVRT activation. Typical: 3–5. Enter 'N/A' if no SVG. Source: SVG firmware.
145 | LVRT/HVRT |  | Hysteresis of WTG kept for LVRT activation de-activation |  | Number | 5 | 0.07 | 0 | 0 | PSSE LVRT Report | Yes | Found | 35 | Hysteresis cycles for WTG LVRT activation. Enter 'N/A' for pure solar. Source: WTG firmware.
146 | LVRT/HVRT |  | LVRT K-Factor As Per Firmware Setting |  | Abs | 5 |  | 0 | 0 | PSSE LVRT Report | Yes | Found | 35 | LVRT K-factor as programmed in inverter/IBR firmware. K-factor = ΔIq / ΔV. Typical range: 2.0–6.0. Must match OEM documentation and be consistent with simulation model.
147 | LVRT/HVRT |  | LVRT K-Factor as per Simulation Model |  | Abs | 2.0 | 2 | 0 | 0 | Firmware Doc | No | Missing: Firmware Doc | 12 | LVRT K-factor as used in PSSE & PSCAD (EMT) simulation model. Must match firmware K-factor (Sr.33). If different, justification required. Source: PSSE & PSSE & PSCAD model documentation.
148 | LVRT/HVRT |  | PPC single phase (LVRT/HVRT) detection available |  | Yes/No | Yes | Yes | NA | NA |  |  |  | 22 | Confirm PSSE & PSCAD model includes logic for single-phase (asymmetric) LVRT/HVRT detection by PPC. Required for unbalanced fault compliance. Expected: 'Yes'. Source: PSSE & PSCAD model.
149 | LVRT/HVRT |  | Transient current limit of IBR(s) as per model | I_max_simulated | p.u. | 1 | 1 | 0.0001 | 0.0001 |  |  |  |  | Transient current limit (p.u.) of IBR as programmed in the simulation model. This is the maximum instantaneous current the IBR can inject. Typical: 1.1–1.3 p.u. Source: PSSE & PSCAD model settings.
150 | LVRT/HVRT |  | Transient current limit of IBR(s) as per Test Report | I_max_Test | p.u. | 1 | 1 | 0.0001 | 0.0001 |  |  |  |  | Transient current limit (p.u.) from type test report. Must match or align with model value (Sr.63). If different, flag for OEM clarification. Source: IBR type test report.
151 | LVRT/HVRT |  | Hysteresis of Inverter kept for HVRT activation de-activation |  | p.u. | 1 | 0.06 | 0.0001 | 0.0001 |  |  |  |  | HVRT hysteresis cycles for inverter activation/deactivation. Prevents oscillation near HVRT threshold. Typical: 2–5 cycles. Source: IBR firmware documentation.
152 | LVRT/HVRT |  | Hysteresis of SVG kept for HVRT activation de-activation |  | p.u. | 1 | 0.08 | 0.0001 | 0.0001 |  |  |  |  | HVRT hysteresis cycles for SVG. Enter 'N/A' if no SVG. Source: SVG firmware.
153 | LVRT/HVRT |  | Hysteresis of WTG kept for HVRT activation de-activation |  | p.u. | 1 | 0.08 | 0.0001 | 0.0001 |  |  |  |  | HVRT hysteresis cycles for WTG. Enter 'N/A' if pure solar. Source: WTG firmware.
154 | LVRT/HVRT |  | Does Master/Slave PPC freeze occur for all the above cases |  | Yes/No | Yes | Yes | Yes | Yes |  |  |  |  | Does Master/Slave PPC enter HVRT freeze mode correctly? Expected: 'Yes' (PPC should freeze active power commands during HVRT to allow inverters to absorb reactive power). Source: PSSE & PSCAD HVRT report.
155 | LVRT/HVRT |  | Master PPC HVRT Threshold voltage setting |  | p.u. | 1 | 1.13 | 0.0001 | 0.0001 |  |  |  |  | Voltage threshold (p.u.) for Master PPC HVRT mode entry. Typical: 1.10–1.15 p.u. Must match firmware and be stated in PPC methodology document.
156 | LVRT/HVRT |  | Slave PPC HVRT Threshold voltage setting (if available) |  | Number | 1 | NA | 0.0001 | 0.0001 |  |  |  |  | Voltage threshold for Slave PPC HVRT (if applicable). Enter actual firmware value. Enter 'N/A' if no Slave PPC.
157 | LVRT/HVRT |  | HVRT K-factor as per firmware setting |  | Number | 2.5 |  | 0.0001 | 0.0001 |  |  |  |  | HVRT K-factor in firmware. K-factor for HVRT = ΔIq(absorption) / ΔV. Typical range: 2.0–6.0. Source: IBR firmware documentation.
158 | LVRT/HVRT |  | HVRT K-factor as per simulation model (EMT) |  | Number | 2.6 | 2 | 0.0001 | 0.0001 |  |  |  |  | HVRT K-factor in PSSE & PSCAD (EMT) model. Must match firmware K-factor within acceptable tolerance. Source: PSSE & PSCAD model documentation.
159 | LVRT/HVRT |  | HVRT K-factor as per simulation model (RMS) |  | Number | 1.2 |  | 0.0001 | 0.0001 |  |  |  |  | HVRT K-factor in PSS/E (RMS) model. Should be consistent with firmware and PSSE & PSCAD. Source: PSS/E dynamic model documentation.
160 | LVRT/HVRT |  | PPC single phase detection available |  | Yes/No | Yes | Yes | NA | NA |  |  |  |  | Does PPC have single-phase voltage detection for HVRT? Required for asymmetric HVRT compliance. Expected: 'Yes'. Source: PPC technical documentation.
161 | Frequency Response Tests |  | Active Power Response observed in the frequency up (50-50.15 Hz) | Del_P_Freq | p.u. | 0.1 | 0.05 | 0.0001 | 0.0001 |  |  |  |  | Active power response change (p.u.) when grid frequency rises from 50 to 50.15 Hz (slight over-frequency). Inverter should decrease output per configured droop. Source: PSSE & PSCAD/PSS/E frequency response test.
162 | Frequency Response Tests |  | Active Power Response observed in the frequency down (50-49.85 Hz) | Del_P_Freq | p.u. | 0.1 | 0 | 0.0001 | 0.0001 |  |  |  |  | Active power response change (p.u.) when grid frequency drops from 50 to 49.85 Hz (slight under-frequency). Inverter should increase output per droop. Source: Frequency response test.
163 | Frequency Response Tests |  | Active Power Response observed in the frequency up ( >0.3Hz) within 1 second | Del_P_Freq | p.u. | 1 | 1 | 0.0001 | 0.0001 |  |  |  |  | Active power response (p.u.) for frequency deviation >0.3 Hz upward within 1 second (FFR test). CEA requirement: ≥10% of rated capacity must respond within 1 second. Source: Dynamics simulation.
164 | Frequency Response Tests |  | Active Power Response observed in the frequency up ( <-0.3Hz) within 1 second | Del_P_Freq | p.u. | 1 | 1 | 0.0001 | 0.0001 |  |  |  |  | Active power response (p.u.) for frequency deviation <−0.3 Hz downward within 1 second. Same requirement: ≥10% of rated capacity. Source: Dynamics simulation.
165 | Frequency Response Tests |  | MPPC Configured Droop in Percentage |  | % | 1.5 | 5 | 1 | 1 |  |  |  | 23 | MPPC (Master PPC) frequency droop setting in %. Acceptable range per CEA: 3%–6%. Enter exact configured value. Example: '4%' or '5%'. Source: PPC settings screenshot.
166 | Frequency Response Tests |  | Unit IBR /WTG settings configured for frequency control in simulation (snapshots) |  | PNG/JPEG | PNG | PDF | 0.0001 | 0.0001 | unit settings for configuration.png | No | Missing: unit settings for configuration.png | 23 | Attach PNG/JPEG screenshot of IBR/WTG unit-level frequency control settings from simulation model (PSSE & PSCAD/PSS/E). Shows configured droop, dead-band, and Pmax/Pmin. File name format: 'unit_freq_settings_sim.png'.
167 | Frequency Response Tests |  | Unit IBR /WTG settings configured for frequency control in firmware (snapshots) |  | PNG/JPEG | PNG | PDF | 0.0001 | 0.0001 | unit settings for configuration.png | No | Missing: unit settings for configuration.png | 43 | Attach PNG/JPEG screenshot of IBR/WTG unit-level frequency control settings from actual firmware HMI. Must match simulation settings (Sr.80). File name: 'unit_freq_settings_fw.png'.
168 | Dynamic Reactive Power Capability Tests |  | MPPC Voltage Droop Setting |  | % | 1.5 | 3 | 0.0001 | 0.0001 |  |  |  |  | MPPC voltage droop setting (%). Used for reactive power regulation. Typical range: 2%–5%. Enter exact configured value. Source: PPC settings documentation.
169 | Dynamic Reactive Power Capability Tests |  | MPPC Reactive Power Limits (Qmax/Qmin) |  | MVAr | 90 | 50.49/-50.49 | NA | NA |  |  |  |  | Maximum and minimum reactive power (MVAr) limits as configured in MPPC. Format: 'Qmax/Qmin in MVAr'. Example: '±90 MVAr'. Must be consistent with PQ capability curve. Source: PPC settings.
170 | Dynamic Reactive Power Capability Tests |  | MPPC Aggregated SVG Reactive Power Limits (Qmax/Qmin) |  | MVAr | 90 | 60/-60 | NA | NA |  |  |  |  | Aggregated SVG reactive power limits (Qmax/Qmin in MVAr) as seen by MPPC. Enter 'N/A' if no SVG. Must match SVG PQ capability. Source: PPC settings + SVG datasheet.
171 | Dynamic Reactive Power Capability Tests |  | MPPC Aggregated IBR/WTG Reactive Power Limits (Qmax/Qmin) |  | MVAr | 90 | 51.15/-51.15 | NA | NA |  |  |  |  | Aggregated IBR/WTG reactive power limits (Qmax/Qmin in MVAr) as configured in MPPC. Must match total plant PQ capability curve at POI. Source: PPC settings.
172 | Ramping Capability Tests |  | MPPC Ramp-Rate setting in PSCAD |  | MW/min | 1 | 15.29 | 0.0001 | 0.0001 |  |  |  |  | MW per minute ramp rate setting in PSSE & PSCAD model for MPPC. Must be consistent with Grid Code requirements (typically ≤10 MW/min per 100 MW or as configured). Source: PSSE & PSCAD PPC model.
173 | Ramping Capability Tests |  | MPPC Active Power Max/Min Setting (Pmax/Pmin) |  | MW | 300 | 153/0 | NA | NA |  |  |  |  | Pmax and Pmin (MW) configured in MPPC for active power dispatch. Format: 'Pmax/Pmin in MW'. Example: '500 MW / 0 MW'. Source: PPC commissioning settings.
174 | Ramping Capability Tests |  | MPPC Polling Rate |  | Samples/Second | NA | 0.02 | 10 | 10 |  |  |  |  | MPPC polling rate in samples/second. This is how often the PPC reads measurements and updates commands. Minimum required: ≥10 samples/sec (per CEA advisory). Source: PPC technical specification.
175 | Ramping Capability Tests |  | IBR Sampling Rate |  | Samples/Second | NA | 0.3 | 10 | 10 |  |  |  |  | IBR unit sampling rate in samples/second. Must be ≥10 samples/sec. If less (e.g., 5/sec), flag as a compliance risk and seek OEM clarification. Source: IBR technical specification.
176 | Ramping Capability Tests |  | MPPC-IBR Command Delay (communication channel) |  | miliseconds | 10 | 25 | NA | NA |  |  |  |  | Communication delay (ms) between MPPC and IBR. Include network/protocol delays. Typical: 10–50 ms. Delays >100 ms may impact frequency response compliance. Source: Communication network design.
177 | Ramping Capability Tests |  | MPPC-SVG Command Delay (communication channel) |  | miliseconds | 10 | 100 | NA | NA |  |  |  |  | Communication delay (ms) between MPPC and SVG. Enter 'N/A' if no SVG. Typical: 10–50 ms. Source: Communication network design.
178 | Ramping Capability Tests |  | MPPC PLC communication protocol details (Ethernet/TCP-IP/ModBus etc.) |  | Protocol Name | NA | NA | NA | NA
The Applicant is required to fill in yellow-highlighted cells only. All remaining fields are system-locked and pre-populated for reference.
Note on L150: Missing: - Firmware Doc
Note on L169: Missing: - unit settings for configuration.png
Note on L170: Missing: - unit settings for configuration.png

## Visual_Data_Dynamic_RE
Visual Data for Total Active Current during LVRT faults (Vdip = 0.15, 0.5,0.85) , SELECT-: Dynamic Data-RE (Category: Id_INV/Id_INV_max/ Id_WTG/ Id_PCS) | Visual Data for Total Active Current during HVRT faults (Vdip = 1.1, 1.2,1.3) , SELECT-: Dynamic Data-RE (Category: Id_INV/Id_INV_max/ Id_WTG/ Id_PCS) |  | Visual Data for RMS Current during LVRT 3-PH faults (Vdip = 0.15, 0.5,0.85) , SELECT-: Dynamic Data-RE (Category: Irms_3PH_INV_max /Irms_3PH_WTG / Irms_3PH_PCS) | Visual Data for Total Reactive Current during LVRT faults (Vdip = 0.15, 0.5,0.85) , SELECT-: Dynamic Data-RE (Category:Iq_f = Iq_pref + Del_Iq) |  | Visual Data for Total Reactive Current during HVRT faults (Vdip = 1.1, 1.2,1.3) , SELECT-: Dynamic Data-RE (Category:Iq_f = Iq_pref + Del_Iq) |  | Visual Data for Total Reactive Power-Capability , SELECT-: Steady State - Q_POI/ Q_INV/ Q_WTG/ Q_SVG
Visual Data for Incremental Reactive Current during LVRT 3-PH faults (Vdip = 0.15, 0.5,0.85) , SELECT-: Dynamic Data-RE (Category: Del_Iq) |  | Visual Data for Incremental Reactive Current Reactive Current during HVRT faults (Vdip = 1.1, 1.2,1.3) , SELECT-: Dynamic Data-RE (Category: Del_Iq) | Visual Data for Incremental Reactive Current during LVRT 2-phase faults (Vdip = 0.15, 0.5,0.85) , SELECT-: Dynamic Data-RE (Category: Del_Iq+/Iq-) |  | Visual Data for Total Reactive Current during LVRT 2-phase faults (Vdip = 0.15, 0.5,0.85) , SELECT-: Dynamic Data-RE (Category: Iq_f = Iq_pref + Del_Iq) |  | Visual Data for Power-Quality (Current Distortion)

## Standard Test Cases
Standard Test Cases for Renewable Energy Sources
Test No. | Unit level(UIBR), USVG/Plant level(P) | Type of Study | Test Type | Parameters | Key Parameters (auto) | Domain (RMS/ EMT) | File Name(pdf) | Found? - File Name(pdf) | Remarks on Files Found | File Name(PSSE/PSCAD) | Found? - File Name(PSSE/PSCAD) | Remarks on Files Found | Compliance Observed | Remarks | 📝 Developer Guidance / Explanatory Note
1 | UIBR | Steady State | PQ Capability Curve of IBR / WTG | POI Voltage (pu) - 1 | POI Voltage (pu) - 1 | RMS | TC_001_RMS_Results.pdf | No | Missing: TC_001_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | PQ Capability Curve Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach the P-Q diagram showing full reactive capability at this POI voltage. Must cover the entire operating range from maximum absorption to maximum injection. ▶ File Name (Sim): Provide 'test.sav' steady-state model file used to generate the PQ curve.
2 | UIBR | Steady State | PQ Capability Curve of IBR / WTG | POI Voltage (pu) - 0.95 | POI Voltage (pu) - 0.95 | RMS | TC_002_RMS_Results.pdf | No | Missing: TC_002_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | PQ Capability Curve Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach the P-Q diagram showing full reactive capability at this POI voltage. Must cover the entire operating range from maximum absorption to maximum injection. ▶ File Name (Sim): Provide 'test.sav' steady-state model file used to generate the PQ curve.
3 | UIBR | Steady State | PQ Capability Curve of IBR / WTG | POI Voltage (pu) - 1.05 | POI Voltage (pu) - 1.05 | RMS | TC_003_RMS_Results.pdf | No | Missing: TC_003_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | PQ Capability Curve Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach the P-Q diagram showing full reactive capability at this POI voltage. Must cover the entire operating range from maximum absorption to maximum injection. ▶ File Name (Sim): Provide 'test.sav' steady-state model file used to generate the PQ curve
4 | UIBR | Dynamic | Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation | POI Voltage:1; Frequency change (Hz): 50 to 47.7 Hz; Power Factor: Any | Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation; POI Voltage:1; Frequency change (Hz): 50 to 47.7 Hz; Power Factor: Any | RMS | TC_004_RMS_Results.pdf | No | Missing: TC_004_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
5 | UIBR | Dynamic | Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation | POI Voltage:1; Frequency Change (Hz): 50 to 47.7 Hz; Power Factor: Any | Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation; POI Voltage:1; Frequency Change (Hz): 50 to 47.7 Hz; Power Factor: Any | RMS | TC_005_RMS_Results.pdf | No | Missing: TC_005_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
6 | UIBR | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | POI Voltage: 0.95 Frequency Change (Hz): 50 to 49.5 Hz; Power Factor: 0.95 Lagging Active Power Dispatch(pu) - 1.0 pu | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation; POI Voltage: 0.95 Frequency Change (Hz): 50 to 49.5 Hz; Power Factor: 0.95 Lagging Active Power Dispatch(pu) - 1.0 pu; Lagging (0.95) | RMS | TC_006_RMS_Results.pdf | No | Missing: TC_006_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
7 | UIBR | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | POI Voltage: 1.05 Frequency Change (Hz): 50 to 49.5 Hz; Power Factor: 0.95 Leading Active Power Dispatch(pu) - 1.0 pu | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation; POI Voltage: 1.05 Frequency Change (Hz): 50 to 49.5 Hz; Power Factor: 0.95 Leading Active Power Dispatch(pu) - 1.0 pu; Leading (0.95) | RMS | TC_007_RMS_Results.pdf | No | Missing: TC_007_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
8 | UIBR | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | POI Voltage: 0.95 Frequency Change (Hz): 50 to 50.5 Hz; Power Factor: 0.95 Lagging Active Power Dispatch(pu) - 1.0 pu | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation; POI Voltage: 0.95 Frequency Change (Hz): 50 to 50.5 Hz; Power Factor: 0.95 Lagging Active Power Dispatch(pu) - 1.0 pu; Lagging (0.95) | RMS | TC_008_RMS_Results.pdf | No | Missing: TC_008_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
9 | UIBR | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | POI Voltage: 1.05 Frequency Change (Hz): 50 to 50.5 Hz; Power Factor: 0.95 Leading Active Power Dispatch(pu) - 1.0 pu | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation; POI Voltage: 1.05 Frequency Change (Hz): 50 to 50.5 Hz; Power Factor: 0.95 Leading Active Power Dispatch(pu) - 1.0 pu; Leading (0.95) | RMS | TC_009_RMS_Results.pdf | No | Missing: TC_009_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
10 | UIBR | Dynamic | Low voltage ride through | LVRT Target voltge(pu) - 0.85 Duration of voltage dip(sec) - 3.0 sec Pre-fault Active Power Dispatch(pu) - 1.0 Nature of voltage dip - Balanced Three Phase | Low voltage ride through; LVRT Target voltge(pu) - 0.85 Duration of voltage dip(sec) - 3.0 sec Pre-fault Active Power Dispatch(pu) - 1.0 Nature of voltage dip - Balanced Three Phase; Balanced Three Phase | RMS | TC_010_RMS_Results.pdf | No | Missing: TC_010_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
11 | UIBR | Dynamic | Low voltage ride through | LVRT Target voltge(pu) - 0.5 Duration of voltage dip(sec) - 1.65 sec Pre-fault Active Power Dispatch(pu) - 1.0 Nature of voltage dip - Balanced Three Phase | Low voltage ride through; LVRT Target voltge(pu) - 0.5 Duration of voltage dip(sec) - 1.65 sec Pre-fault Active Power Dispatch(pu) - 1.0 Nature of voltage dip - Balanced Three Phase; Balanced Three Phase | RMS | TC_011_RMS_Results.pdf | No | Missing: TC_011_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
12 | UIBR | Dynamic | Low voltage ride through | LVRT Target voltge(pu) - 0.15 Duration of voltage dip(sec) - 0.3 sec Pre-fault Active Power Dispatch(pu) - 1.0 Nature of voltage dip - Balanced Three Phase | Low voltage ride through; LVRT Target voltge(pu) - 0.15 Duration of voltage dip(sec) - 0.3 sec Pre-fault Active Power Dispatch(pu) - 1.0 Nature of voltage dip - Balanced Three Phase; Balanced Three Phase | RMS | TC_012_RMS_Results.pdf | No | Missing: TC_012_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
13 | UIBR | Dynamic | Low voltage ride through | LVRT Target voltge(pu) - 0.85 Duration of voltage dip(sec) - 3 sec Pre-fault Active Power Dispatch(pu) - 0.5 Nature of voltage dip - Balanced Three Phase | Low voltage ride through; LVRT Target voltge(pu) - 0.85 Duration of voltage dip(sec) - 3 sec Pre-fault Active Power Dispatch(pu) - 0.5 Nature of voltage dip - Balanced Three Phase; Balanced Three Phase | RMS | TC_013_RMS_Results.pdf | No | Missing: TC_013_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
14 | UIBR | Dynamic | Low voltage ride through | LVRT Target voltge(pu) - 0.5 Duration of voltage dip(sec) - 1.65 sec Pre-fault Active Power Dispatch(pu) - 0.5 pu Nature of voltage dip - Balanced Three Phase | Low voltage ride through; LVRT Target voltge(pu) - 0.5 Duration of voltage dip(sec) - 1.65 sec Pre-fault Active Power Dispatch(pu) - 0.5 pu Nature of voltage dip - Balanced Three Phase; Balanced Three Phase | RMS | TC_014_RMS_Results.pdf | No | Missing: TC_014_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
15 | UIBR | Dynamic | Low voltage ride through | LVRT Target voltge(pu) - 0.5 Duration of voltage dip(sec) - 0.3 sec Pre-fault Active Power Dispatch(pu) - 0.5 pu Nature of voltage dip - Balanced Three Phase | Low voltage ride through; LVRT Target voltge(pu) - 0.5 Duration of voltage dip(sec) - 0.3 sec Pre-fault Active Power Dispatch(pu) - 0.5 pu Nature of voltage dip - Balanced Three Phase; Balanced Three Phase | RMS | TC_015_RMS_Results.pdf | No | Missing: TC_015_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
16 | UIBR | Dynamic | Low voltage ride through | LVRT Target voltge(pu) - 0.85 Duration of voltage dip(sec) - 3.0 sec Pre-fault Active Power Dispatch(pu) - 0.25 Nature of voltage dip - Balanced Three Phase | Low voltage ride through; LVRT Target voltge(pu) - 0.85 Duration of voltage dip(sec) - 3.0 sec Pre-fault Active Power Dispatch(pu) - 0.25 Nature of voltage dip - Balanced Three Phase; Balanced Three Phase | RMS | TC_016_RMS_Results.pdf | No | Missing: TC_016_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
17 | UIBR | Dynamic | Low voltage ride through | LVRT Target voltge(pu) - 0.5 Duration of voltage dip(sec) - 1.65 sec Pre-fault Active Power Dispatch(pu) - 0.25 Nature of voltage dip - Balanced Three Phase | Low voltage ride through; LVRT Target voltge(pu) - 0.5 Duration of voltage dip(sec) - 1.65 sec Pre-fault Active Power Dispatch(pu) - 0.25 Nature of voltage dip - Balanced Three Phase; Balanced Three Phase | RMS | TC_017_RMS_Results.pdf | No | Missing: TC_017_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
18 | UIBR | Dynamic | Low voltage ride through | LVRT Target voltge(pu) - 0.15 Duration of voltage dip(sec) - 0.3 sec Pre-fault Active Power Dispatch(pu) - 0.25 Nature of voltage dip - Balanced Three Phase | Low voltage ride through; LVRT Target voltge(pu) - 0.15 Duration of voltage dip(sec) - 0.3 sec Pre-fault Active Power Dispatch(pu) - 0.25 Nature of voltage dip - Balanced Three Phase | RMS | TC_018_RMS_Results.pdf | No | Missing: TC_018_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
19 | UIBR | Dynamic | Active power set-point and Rate of change of active power | Active power set-point and Ramp up test(ramp rate < 10% per minute) POI Voltage - 1.0 pu | Active power set-point and Rate of change of active power; Active power set-point and Ramp up test(ramp rate < 10% per minute) POI Voltage - 1.0 pu | RMS | TC_019_RMS_Results.pdf | No | Missing: TC_019_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Ramp Rate / Active Power Set-point Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing ramp-up/ramp-down power response over time. Plot must show ramp rate (MW/min) and confirm it is ≤10% of rated per minute. ▶ File Name (Sim): Provide 'test.sav' model file for this ramp test. ▶ Key check: Ramp rate ≤10% of rated MW per minute as required by CEA/Grid Code.
20 | UIBR | Dynamic | Active power set-point and Rate of change of active power | Active power set-point and Ramp down test (ramp rate < 10% per minute) POI Voltage - 1.0 pu | Active power set-point and Rate of change of active power; Active power set-point and Ramp down test (ramp rate < 10% per minute) POI Voltage - 1.0 pu; POI Voltage - 1.0 pu | RMS | TC_020_RMS_Results.pdf | No | Missing: TC_020_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Ramp Rate / Active Power Set-point Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing ramp-up/ramp-down power response over time. Plot must show ramp rate (MW/min) and confirm it is ≤10% of rated per minute. ▶ File Name (Sim): Provide 'test.sav' model file for this ramp test. ▶ Key check: Ramp rate ≤10% of rated MW per minute as required by CEA/Grid Code.
21 | UIBR | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency Change: 50 to 50.15 Hz Active Power Dispatch(pu): 0.9 - 1.0 POI/PCC Voltage(pu) - 1.0 Power Factor(pf): Unity | Frequency response test (any droop in range of 3 - 6%); Frequency Change: 50 to 50.15 Hz Active Power Dispatch(pu): 0.9 - 1.0 POI/PCC Voltage(pu) - 1.0 Power Factor(pf): Unity | RMS | TC_021_RMS_Results.pdf | No | Missing: TC_021_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
22 | UIBR | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency Change: 50 to 50.15 Hz Active Power Dispatch(pu): 0.5 POI/PCC Voltage(pu) - 1.0 Power Factor(pf): Unity | Frequency response test (any droop in range of 3 - 6%); Frequency Change: 50 to 50.15 Hz Active Power Dispatch(pu): 0.5 POI/PCC Voltage(pu) - 1.0 Power Factor(pf): Unity | RMS | TC_022_RMS_Results.pdf | No | Missing: TC_022_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
23 | UIBR | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency Change: 50 to 50.15 Hz Active Power Dispatch(pu): 0.1 POI/PCC Voltage(pu) - 1.0 Power Factor(pf) - Unity | Frequency response test (any droop in range of 3 - 6%); Frequency Change: 50 to 50.15 Hz Active Power Dispatch(pu): 0.1 POI/PCC Voltage(pu) - 1.0 Power Factor(pf) - Unity | RMS | TC_023_RMS_Results.pdf | No | Missing: TC_023_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
24 | UIBR | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency Change: 50 to 49.85 Hz Active Power Dispatch(pu): 0.5 POI/PCC Voltage(pu) - 1.0 Power Factor(pf) - Unity | Frequency response test (any droop in range of 3 - 6%); Frequency Change: 50 to 49.85 Hz Active Power Dispatch(pu): 0.5 POI/PCC Voltage(pu) - 1.0 Power Factor(pf) - Unity | RMS | TC_024_RMS_Results.pdf | No | Missing: TC_024_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
25 | UIBR | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency Change: 50 to 49.85 Hz Active Power Dispatch(pu): 0.1 POI/PCC Voltage(pu) - 1.0 Power Factor(pf) - Unity | Frequency response test (any droop in range of 3 - 6%); Frequency Change: 50 to 49.85 Hz Active Power Dispatch(pu): 0.1 POI/PCC Voltage(pu) - 1.0 Power Factor(pf) - Unity | RMS | TC_025_RMS_Results.pdf | No | Missing: TC_025_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
26 | UIBR | Dynamic | Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz | Greater than 0.3Hz (upwards) Active Power Dispatch(pu): 0.9 - 1.0 POI/PCC Voltage (pu) - 1.0 Power factor(pf) - Unity | Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz; Greater than 0.3Hz (upwards) Active Power Dispatch(pu): 0.9 - 1.0 POI/PCC Voltage (pu) - 1.0 Power factor(pf) - Unity | RMS | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
27 | UIBR | Dynamic | Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz | Greater than 0.3Hz (downwards) Active Power Dispatch(pu): 0.9 - 1.0 POI/PCC Voltage (pu) - 1.0 Power factor(pf) - Unity | Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz; Greater than 0.3Hz (downwards) Active Power Dispatch(pu): 0.9 - 1.0 POI/PCC Voltage (pu) - 1.0 Power factor(pf) - Unity | RMS | TC_027_RMS_Results.pdf | No | Missing: TC_027_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
28 | UIBR | Dynamic | High voltage ride through | HVRT Target Voltage (pu) - 1.3 Duration of voltage rise (sec) - 0.2 Initial Active Power dispatch (pu) - 1.0 Nature of voltage rise - Balanced Three phase | High voltage ride through; HVRT Target Voltage (pu) - 1.3 Duration of voltage rise (sec) - 0.2 Initial Active Power dispatch (pu) - 1.0 Nature of voltage rise - Balanced Three phase; Balanced Three Phase | RMS | TC_028_RMS_Results.pdf | No | Missing: TC_028_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
29 | UIBR | Dynamic | High voltage ride through | HVRT Target Voltage (pu) - 1.2 Duration of voltage rise (sec) - 2 Initial Active Power dispatch (pu) - 1.0 Nature of voltage rise - Balanced Three phase | High voltage ride through; HVRT Target Voltage (pu) - 1.2 Duration of voltage rise (sec) - 2 Initial Active Power dispatch (pu) - 1.0 Nature of voltage rise - Balanced Three phase; Balanced Three Phase | RMS | TC_029_RMS_Results.pdf | No | Missing: TC_029_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
30 | UIBR | Dynamic | High voltage ride through | HVRT Target Voltage (pu) - 1.3 Duration of voltage rise (sec) - 0.2 Initial Active Power dispatch (pu) - 0.5 Nature of voltage rise - Balanced Three phase | High voltage ride through; HVRT Target Voltage (pu) - 1.3 Duration of voltage rise (sec) - 0.2 Initial Active Power dispatch (pu) - 0.5 Nature of voltage rise - Balanced Three phase; Balanced Three Phase | RMS | TC_030_RMS_Results.pdf | No | Missing: TC_030_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
31 | UIBR | Dynamic | High voltage ride through | HVRT Target Voltage (pu) - 1.2 Duration of voltage rise (sec) - 2 Initial Active Power dispatch (pu) - 0.5 Nature of voltage rise - Balanced Three phase | High voltage ride through; HVRT Target Voltage (pu) - 1.2 Duration of voltage rise (sec) - 2 Initial Active Power dispatch (pu) - 0.5 Nature of voltage rise - Balanced Three phase; Balanced Three Phase | RMS | TC_031_RMS_Results.pdf | No | Missing: TC_031_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
32 | UIBR | Dynamic | High voltage ride through | HVRT Target Voltage (pu) - 1.3 Duration of voltage rise (sec) - 0.2 Initial Active Power dispatch (pu) - 0.25 Nature of voltage rise - Balanced Three phase | High voltage ride through; HVRT Target Voltage (pu) - 1.3 Duration of voltage rise (sec) - 0.2 Initial Active Power dispatch (pu) - 0.25 Nature of voltage rise - Balanced Three phase; Balanced Three Phase | RMS | TC_032_RMS_Results.pdf | No | Missing: TC_032_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
33 | UIBR | Dynamic | High voltage ride through | HVRT Target Voltage (pu) - 1.2 Duration of voltage rise (sec) - 2 Initial Active Power dispatch (pu) - 0.25 Nature of voltage rise - Balanced Three phase | High voltage ride through; HVRT Target Voltage (pu) - 1.2 Duration of voltage rise (sec) - 2 Initial Active Power dispatch (pu) - 0.25 Nature of voltage rise - Balanced Three phase; Balanced Three Phase | RMS | TC_033_RMS_Results.pdf | No | Missing: TC_033_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
34 | UIBR | Steady State | PQ Capability Curve of IBR / WTG | POI/PCC Voltage (pu) - 1.0 |  | EMT | TC_034_EMT_Results.pdf | No | Missing: TC_034_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | PQ Capability Curve Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the P-Q diagram showing full reactive capability at this POI voltage. Must cover the entire operating range from maximum absorption to maximum injection. ▶ File Name (Sim): Provide 'test.pscx' steady-state model file used to generate the PQ curve. ▶ Key check: PQ envelope must meet CEA grid code requirements (0.95 pf lag to 0.95 pf lead at rated P).
35 | UIBR | Steady State | PQ Capability Curve of IBR / WTG | POI/PCC Voltage (pu) -0.95 |  | EMT | TC_035_EMT_Results.pdf | No | Missing: TC_035_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | PQ Capability Curve Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the P-Q diagram showing full reactive capability at this POI voltage. Must cover the entire operating range from maximum absorption to maximum injection. ▶ File Name (Sim): Provide 'test.pscx' steady-state model file used to generate the PQ curve. ▶ Key check: PQ envelope must meet CEA grid code requirements (0.95 pf lag to 0.95 pf lead at rated P).
36 | UIBR | Steady State | PQ Capability Curve of IBR / WTG | POI/PCC Voltage (pu) -1.05 |  | EMT | TC_036_EMT_Results.pdf | No | Missing: TC_036_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | PQ Capability Curve Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the P-Q diagram showing full reactive capability at this POI voltage. Must cover the entire operating range from maximum absorption to maximum injection. ▶ File Name (Sim): Provide 'test.pscx' steady-state model file used to generate the PQ curve. ▶ Key check: PQ envelope must meet CEA grid code requirements (0.95 pf lag to 0.95 pf lead at rated P).
37 | UIBR | Dynamic | Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 47.5; POI Voltage (pu): 1; Power factor: Any; | Frequency change (Hz): 50 to 47.5; POI Voltage (pu): 1; Power factor: Any; Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation | EMT | TC_037_EMT_Results.pdf | No | Missing: TC_037_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
38 | UIBR | Dynamic | Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 52; POI Voltage (pu): 1; Power factor: Any; | Frequency change (Hz): 50 to 52; POI Voltage (pu): 1; Power factor: Any; Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation | EMT | TC_038_EMT_Results.pdf | No | Missing: TC_038_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
39 | UIBR | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 49.5; POI /PCC Voltage (pu): 0.95; Power factor (pf): Lagging (0.95); Active Power dispatch (pu): 1; | Frequency change (Hz): 50 to 49.5; POI /PCC Voltage (pu): 0.95; Power factor (pf): Lagging (0.95); Active Power dispatch (pu): 1; Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation; Lagging (0.95) | EMT | TC_039_EMT_Results.pdf | No | Missing: TC_039_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
40 | UIBR | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | POI /PCC Voltage (pu): 1.05; Power factor (pf): Leading (0.95); Active Power dispatch (pu): 1; | POI /PCC Voltage (pu): 1.05; Power factor (pf): Leading (0.95); Leading (0.95) | EMT | TC_040_EMT_Results.pdf | No | Missing: TC_040_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
41 | UIBR | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 50.5; POI /PCC Voltage (pu): 0.95; Power factor (pf): Lagging (0.95); Active Power dispatch (pu): 1; | Frequency change (Hz): 50 to 50.5; POI /PCC Voltage (pu): 0.95; Power factor (pf): Lagging (0.95); Active Power dispatch (pu): 1; Lagging (0.95) | EMT | TC_041_EMT_Results.pdf | No | Missing: TC_041_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
42 | UIBR | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | POI /PCC Voltage (pu): 1.05; Power factor (pf): Leading (0.95); Active Power dispatch (pu): 1; | POI /PCC Voltage (pu): 1.05; Power factor (pf): Leading (0.95); Leading (0.95) | EMT | TC_042_EMT_Results.pdf | No | Missing: TC_042_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
43 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced Three phase; ; Balanced Three phase | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced Three phase; Low Voltage Ride Through (LVRT); Balanced Three phase | EMT | TC_043_EMT_Results.pdf | No | Missing: TC_043_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
44 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced Three phase; ; Balanced Three phase | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced Three phase; Low Voltage Ride Through (LVRT); Balanced Three phase | EMT | TC_044_EMT_Results.pdf | No | Missing: TC_044_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
45 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced Three phase; ; Balanced Three phase | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced Three phase; Low Voltage Ride Through (LVRT); Balanced Three phase | EMT | TC_045_EMT_Results.pdf | No | Missing: TC_045_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
46 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced (LL); ; Unbalanced (LL) | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced (LL); Low Voltage Ride Through (LVRT); Unbalanced (LL) | EMT | TC_046_EMT_Results.pdf | No | Missing: TC_046_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
47 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced (LL); ; Unbalanced (LL) | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced (LL); Low Voltage Ride Through (LVRT); Unbalanced (LL) | EMT | TC_047_EMT_Results.pdf | No | Missing: TC_047_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
48 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced (LL); ; Unbalanced (LL) | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced (LL); Low Voltage Ride Through (LVRT); Unbalanced (LL) | EMT | TC_048_EMT_Results.pdf | No | Missing: TC_048_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
49 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced (L); | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced (L); Low Voltage Ride Through (LVRT); Unbalanced (L) | EMT | TC_049_EMT_Results.pdf | No | Missing: TC_049_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
50 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced (L); | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced (L); Low Voltage Ride Through (LVRT); Unbalanced (L) | EMT | TC_050_EMT_Results.pdf | No | Missing: TC_050_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
51 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced (L); | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced (L); Low Voltage Ride Through (LVRT); Unbalanced (L) | EMT | TC_051_EMT_Results.pdf | No | Missing: TC_051_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
52 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced Three phase; Low Voltage Ride Through (LVRT); Balanced Three phase | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced Three phase; Low Voltage Ride Through (LVRT); Balanced Three phase | EMT | TC_052_EMT_Results.pdf | No | Missing: TC_052_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
53 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced Three phase; Low Voltage Ride Through (LVRT); Balanced Three phase | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced Three phase; Low Voltage Ride Through (LVRT); Balanced Three phase | EMT | TC_053_EMT_Results.pdf | No | Missing: TC_053_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
54 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced Three phase; Low Voltage Ride Through (LVRT); Balanced Three phase | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced Three phase; Low Voltage Ride Through (LVRT); Balanced Three phase | EMT | TC_054_EMT_Results.pdf | No | Missing: TC_054_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
55 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced (LL); Low Voltage Ride Through (LVRT); Unbalanced (LL) | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced (LL); Low Voltage Ride Through (LVRT); Unbalanced (LL) | EMT | TC_055_EMT_Results.pdf | No | Missing: TC_055_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
56 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced (LL); Low Voltage Ride Through (LVRT); Unbalanced (LL) | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced (LL); Low Voltage Ride Through (LVRT); Unbalanced (LL) | EMT | TC_056_EMT_Results.pdf | No | Missing: TC_056_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
57 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced (LL); Low Voltage Ride Through (LVRT); Unbalanced (LL) | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced (LL); Low Voltage Ride Through (LVRT); Unbalanced (LL) | EMT | TC_057_EMT_Results.pdf | No | Missing: TC_057_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
58 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced (L); | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced (L); Low Voltage Ride Through (LVRT); Unbalanced (L) | EMT | TC_058_EMT_Results.pdf | No | Missing: TC_058_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
59 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced (L); | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced (L); Low Voltage Ride Through (LVRT); Unbalanced (L) | EMT | TC_059_EMT_Results.pdf | No | Missing: TC_059_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
60 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced (L); | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced (L); Low Voltage Ride Through (LVRT); Unbalanced (L) | EMT | TC_060_EMT_Results.pdf | No | Missing: TC_060_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
61 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced Three phase; Low Voltage Ride Through (LVRT); Balanced Three phase | EMT | TC_061_EMT_Results.pdf | No | Missing: TC_061_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
62 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced Three phase; Low Voltage Ride Through (LVRT); Balanced Three phase | EMT | TC_062_EMT_Results.pdf | No | Missing: TC_062_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
63 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced Three phase; Low Voltage Ride Through (LVRT); Balanced Three phase | EMT | TC_063_EMT_Results.pdf | No | Missing: TC_063_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
64 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced (LL); | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced (LL); Low Voltage Ride Through (LVRT); Unbalanced (LL) | EMT | TC_064_EMT_Results.pdf | No | Missing: TC_064_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
65 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced (LL); | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced (LL); Low Voltage Ride Through (LVRT); Unbalanced (LL) | EMT | TC_065_EMT_Results.pdf | No | Missing: TC_065_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
66 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced (LL); | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced (LL); Low Voltage Ride Through (LVRT); Unbalanced (LL) | EMT | TC_066_EMT_Results.pdf | No | Missing: TC_066_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
67 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced (L); | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced (L); Low Voltage Ride Through (LVRT); Unbalanced (L) | EMT | TC_067_EMT_Results.pdf | No | Missing: TC_067_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
68 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced (L); | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced (L); Low Voltage Ride Through (LVRT); Unbalanced (L) | EMT | TC_068_EMT_Results.pdf | No | Missing: TC_068_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
69 | UIBR | Dynamic | Low Voltage Ride Through (LVRT) | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced (L); | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre - fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced (L); Low Voltage Ride Through (LVRT); Unbalanced (L) | EMT | TC_069_EMT_Results.pdf | No | Missing: TC_069_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
70 | UIBR | Dynamic | Active power set-point and Rate of change of active power | Change in active power dispatch: Active power set-point and Ramp up test (ramp rate < 10% per minute); POI/PCC Voltage (pu): 1; Power factor (pf): Unity; | Change in active power dispatch: Active power set-point and Ramp up test (ramp rate < 10% per minute); POI/PCC Voltage (pu): 1; Power factor (pf): Unity; Active power set-point and Rate of change of active power; Active power set-point and Ramp up test (ramp rate < 10% per minute) | EMT | TC_070_EMT_Results.pdf | No | Missing: TC_070_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Ramp Rate / Active Power Set-point Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing ramp-up/ramp-down power response over time. Plot must show ramp rate (MW/min) and confirm it is ≤10% of rated per minute. ▶ File Name (Sim): Provide 'test.pscx' model file for this ramp test. ▶ Key check: Ramp rate ≤10% of rated MW per minute as required by CEA/Grid Code.
71 | UIBR | Dynamic | Active power set-point and Rate of change of active power | Change in active power dispatch: Active power set-point and Ramp down test (ramp rate < 10% per minute); POI/PCC Voltage (pu): 1; Power factor (pf): Unity; | Change in active power dispatch: Active power set-point and Ramp down test (ramp rate < 10% per minute); POI/PCC Voltage (pu): 1; Power factor (pf): Unity; Active power set-point and Rate of change of active power; Active power set-point and Ramp down test (ramp rate < 10% per minute) | EMT | TC_071_EMT_Results.pdf | No | Missing: TC_071_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Ramp Rate / Active Power Set-point Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing ramp-up/ramp-down power response over time. Plot must show ramp rate (MW/min) and confirm it is ≤10% of rated per minute. ▶ File Name (Sim): Provide 'test.pscx' model file for this ramp test. ▶ Key check: Ramp rate ≤10% of rated MW per minute as required by CEA/Grid Code.
72 | UIBR | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 0.9-1.0; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 0.9-1.0; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; Frequency response test (any droop in range of 3 - 6%) | EMT | TC_072_EMT_Results.pdf | No | Missing: TC_072_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
73 | UIBR | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 0.5; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 0.5; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; Frequency response test (any droop in range of 3 - 6%) | EMT | TC_073_EMT_Results.pdf | No | Missing: TC_073_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
74 | UIBR | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 0.1; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 0.1; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; Frequency response test (any droop in range of 3 - 6%) | EMT | TC_074_EMT_Results.pdf | No | Missing: TC_074_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
75 | UIBR | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 0.5; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 0.5; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; Frequency response test (any droop in range of 3 - 6%) | EMT | TC_075_EMT_Results.pdf | No | Missing: TC_075_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
76 | UIBR | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 0.1; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 0.1; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; Frequency response test (any droop in range of 3 - 6%) | EMT | TC_076_EMT_Results.pdf | No | Missing: TC_076_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
77 | UIBR | Dynamic | Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz: | Change in frequency (Hz): Greater than 0.3Hz (upwards); Active Power dispatch (pu): 1; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz:; Greater than 0.3Hz (upwards) | Change in frequency (Hz): Greater than 0.3Hz (upwards); Active Power dispatch (pu): 1; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz:; Greater than 0.3Hz (upwards) | EMT | TC_077_EMT_Results.pdf | No | Missing: TC_077_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
78 | UIBR | Dynamic | Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz: | Change in frequency (Hz): Greater than 0.3Hz (downwards); Active Power dispatch (pu): 1; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz:; Greater than 0.3Hz (downwards) | Change in frequency (Hz): Greater than 0.3Hz (downwards); Active Power dispatch (pu): 1; POI/PCC Voltage (pu): 1; Power factor (pf): Unity; Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz:; Greater than 0.3Hz (downwards) | EMT | TC_078_EMT_Results.pdf | No | Missing: TC_078_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
79 | UIBR | Dynamic | High Voltage Ride Through (HVRT) | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced Three phase; High Voltage Ride Through (HVRT); Balanced Three phase | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced Three phase; High Voltage Ride Through (HVRT); Balanced Three phase | EMT | TC_079_EMT_Results.pdf | No | Missing: TC_079_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
80 | UIBR | Dynamic | High Voltage Ride Through (HVRT) | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced Three phase; High Voltage Ride Through (HVRT); Balanced Three phase | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced Three phase; High Voltage Ride Through (HVRT); Balanced Three phase | EMT | TC_080_EMT_Results.pdf | No | Missing: TC_080_EMT_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
81 | UIBR | Dynamic | High Voltage Ride Through (HVRT) | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Single phase; High Voltage Ride Through (HVRT); Single phase | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Single phase; High Voltage Ride Through (HVRT); Single phase | EMT | TC_001_RMS_Results.pdf | No | Missing: TC_001_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
82 | UIBR | Dynamic | High Voltage Ride Through (HVRT) | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Single phase; High Voltage Ride Through (HVRT); Single phase | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Single phase; High Voltage Ride Through (HVRT); Single phase | EMT | TC_002_RMS_Results.pdf | No | Missing: TC_002_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
83 | UIBR | Dynamic | High Voltage Ride Through (HVRT) | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced Three phase; High Voltage Ride Through (HVRT); Balanced Three phase | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced Three phase; High Voltage Ride Through (HVRT); Balanced Three phase | EMT | TC_003_RMS_Results.pdf | No | Missing: TC_003_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
84 | UIBR | Dynamic | High Voltage Ride Through (HVRT) | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced Three phase; High Voltage Ride Through (HVRT); Balanced Three phase | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced Three phase; High Voltage Ride Through (HVRT); Balanced Three phase | EMT | TC_004_RMS_Results.pdf | No | Missing: TC_004_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
85 | UIBR | Dynamic | High Voltage Ride Through (HVRT) | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Single phase; High Voltage Ride Through (HVRT); Single phase | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Single phase; High Voltage Ride Through (HVRT); Single phase | EMT | TC_005_RMS_Results.pdf | No | Missing: TC_005_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
86 | UIBR | Dynamic | High Voltage Ride Through (HVRT) | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Single phase; High Voltage Ride Through (HVRT); Single phase | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Single phase; High Voltage Ride Through (HVRT); Single phase | EMT | TC_006_RMS_Results.pdf | No | Missing: TC_006_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
87 | UIBR | Dynamic | High Voltage Ride Through (HVRT) | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Balanced Three phase; High Voltage Ride Through (HVRT); Balanced Three phase | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Balanced Three phase; High Voltage Ride Through (HVRT); Balanced Three phase | EMT | TC_007_RMS_Results.pdf | No | Missing: TC_007_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
88 | UIBR | Dynamic | High Voltage Ride Through (HVRT) | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Balanced Three phase; High Voltage Ride Through (HVRT); Balanced Three phase | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Balanced Three phase; High Voltage Ride Through (HVRT); Balanced Three phase | EMT | TC_008_RMS_Results.pdf | No | Missing: TC_008_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
89 | UIBR | Dynamic | High Voltage Ride Through (HVRT) | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Single phase; High Voltage Ride Through (HVRT); Single phase | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Single phase; High Voltage Ride Through (HVRT); Single phase | EMT | TC_009_RMS_Results.pdf | No | Missing: TC_009_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
90 | UIBR | Dynamic | High Voltage Ride Through (HVRT) | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Single phase; High Voltage Ride Through (HVRT); Single phase | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Single phase; High Voltage Ride Through (HVRT); Single phase | EMT | TC_010_RMS_Results.pdf | No | Missing: TC_010_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: UIBR ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
91 | USVG | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Reactive Power dispatch: Max. absorption; | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Reactive Power dispatch: Max. absorption; Low voltage ride through | RMS | TC_011_RMS_Results.pdf | No | Missing: TC_011_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: USVG ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
92 | USVG | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Reactive Power dispatch: Max. absorption; | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Reactive Power dispatch: Max. absorption; Low voltage ride through | RMS | TC_012_RMS_Results.pdf | No | Missing: TC_012_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: USVG ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
93 | USVG | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Reactive Power dispatch: Max. absorption; | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Reactive Power dispatch: Max. absorption; Low voltage ride through | RMS | TC_013_RMS_Results.pdf | No | Missing: TC_013_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: USVG ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
94 | USVG | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.3; Duration of voltage dip (sec): 0.2; Initial Reactive Power dispatch: Max. injection; | HVRT Target Voltage (pu): 1.3; Duration of voltage dip (sec): 0.2; Initial Reactive Power dispatch: Max. injection; High voltage ride through | RMS | TC_014_RMS_Results.pdf | No | Missing: TC_014_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: USVG ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
95 | USVG | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.2; Duration of voltage dip (sec): 2; Initial Reactive Power dispatch: Max. injection; | HVRT Target Voltage (pu): 1.2; Duration of voltage dip (sec): 2; High voltage ride through | RMS | TC_015_RMS_Results.pdf | No | Missing: TC_015_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: USVG ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
96 | USVG | Dynamic | Demonstration of ± Q capability | Upto full capacitive range | HVRT Target Voltage (pu): Upto full capacitive range; Upto full capacitive range | RMS | TC_016_RMS_Results.pdf | No | Missing: TC_016_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Reactive Power Capability Test ¦ Level: USVG ¦ Domain: RMS ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.sav' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
97 | USVG | Dynamic | Demonstration of ± Q capability | Upto full inductive range | HVRT Target Voltage (pu): Upto full inductive range; Upto full inductive range | RMS | TC_017_RMS_Results.pdf | No | Missing: TC_017_RMS_Results.pdf | test.sav | Yes | Found | Yes |  | Reactive Power Capability Test ¦ Level: USVG ¦ Domain: RMS ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.sav' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
98 | USVG | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Reactive Power dispatch (pu): Max. absorption mode; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Reactive Power dispatch (pu): Max. absorption mode; Nature of voltage dip: Balanced Three phase; Low voltage ride through; Balanced Three phase | EMT | TC_018_RMS_Results.pdf | No | Missing: TC_018_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: USVG ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
99 | USVG | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Reactive Power dispatch (pu): Max. absorption mode; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Reactive Power dispatch (pu): Max. absorption mode; Nature of voltage dip: Balanced Three phase; Low voltage ride through; Balanced Three phase | EMT | TC_019_RMS_Results.pdf | No | Missing: TC_019_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: USVG ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
100 | USVG | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Reactive Power dispatch (pu): Max. absorption mode; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Reactive Power dispatch (pu): Max. absorption mode; Nature of voltage dip: Balanced Three phase; Low voltage ride through; Balanced Three phase | EMT | TC_020_RMS_Results.pdf | No | Missing: TC_020_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: USVG ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
101 | USVG | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Reactive Power dispatch (pu): Max. absorption mode; Nature of voltage dip: Unbalanced (LL); | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Reactive Power dispatch (pu): Max. absorption mode; Nature of voltage dip: Unbalanced (LL); Low voltage ride through; Unbalanced (LL) | EMT | TC_021_RMS_Results.pdf | No | Missing: TC_021_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: USVG ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
102 | USVG | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Reactive Power dispatch (pu): Max. absorption mode; Nature of voltage dip: Unbalanced (LL); | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Reactive Power dispatch (pu): Max. absorption mode; Nature of voltage dip: Unbalanced (LL); Low voltage ride through; Unbalanced (LL) | EMT | TC_022_RMS_Results.pdf | No | Missing: TC_022_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: USVG ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
103 | USVG | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Reactive Power dispatch (pu): Max. absorption mode; Nature of voltage dip: Unbalanced (LL); | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Reactive Power dispatch (pu): Max. absorption mode; Nature of voltage dip: Unbalanced (LL); Low voltage ride through; Unbalanced (LL) | EMT | TC_023_RMS_Results.pdf | No | Missing: TC_023_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: USVG ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
104 | USVG | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.3; Duration of voltage dip (sec): 0.2; Initial Reactive Power dispatch (pu): Max. injection mode; Nature of voltage dip: Balanced Three phase; | HVRT Target Voltage (pu): 1.3; Duration of voltage dip (sec): 0.2; Initial Reactive Power dispatch (pu): Max. injection mode; Nature of voltage dip: Balanced Three phase; High voltage ride through; Balanced Three phase | EMT | TC_024_RMS_Results.pdf | No | Missing: TC_024_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: USVG ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
105 | USVG | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.2; Duration of voltage dip (sec): 2; Initial Reactive Power dispatch (pu): Max. injection mode; Nature of voltage dip: Balanced Three phase; | HVRT Target Voltage (pu): 1.2; Duration of voltage dip (sec): 2; Initial Reactive Power dispatch (pu): Max. injection mode; Nature of voltage dip: Balanced Three phase; High voltage ride through; Balanced Three phase | EMT | TC_025_RMS_Results.pdf | No | Missing: TC_025_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: USVG ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
106 | USVG | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.3; Duration of voltage dip (sec): 0.2; Initial Reactive Power dispatch (pu): Max. injection mode; Nature of voltage dip: Single phase; | HVRT Target Voltage (pu): 1.3; Duration of voltage dip (sec): 0.2; Initial Reactive Power dispatch (pu): Max. injection mode; Nature of voltage dip: Single phase; High voltage ride through; Single phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: USVG ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
107 | USVG | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.2; Duration of voltage dip (sec): 2; Initial Reactive Power dispatch (pu): Max. injection mode; Nature of voltage dip: Single phase; | HVRT Target Voltage (pu): 1.2; Duration of voltage dip (sec): 2; Initial Reactive Power dispatch (pu): Max. injection mode; Nature of voltage dip: Single phase; High voltage ride through; Single phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: USVG ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
108 | USVG | Dynamic | Demonstration of ± Q capability | Upto full capacitive range | HVRT Target Voltage (pu): Upto full capacitive range; Upto full capacitive range | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Reactive Power Capability Test ¦ Level: USVG ¦ Domain: EMT ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.pscx' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
109 | USVG | Dynamic | Demonstration of ± Q capability | Upto full inductive range | HVRT Target Voltage (pu): Upto full inductive range; Upto full inductive range | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Reactive Power Capability Test ¦ Level: USVG ¦ Domain: EMT ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.pscx' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
110 | PEMT | Power Quality | Evaluation of current harmonics at POI (Harmonic Load Flow model) | P=1.0; | HVRT Target Voltage (pu): P=1.0; Evaluation of current harmonics at POI (Harmonic Load Flow model); P=1.0 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Power Quality / Harmonic Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach harmonic load flow results showing current harmonic spectrum at POI for each active power level. Verify TDD ≤1.5% and band limits per CEA connectivity standards. ▶ File Name (Sim): Provide 'test.pscx' PSCAD model file including harmonic injection sources. ▶ Key check: All harmonic distortion values must be within CEA Connectivity Standard limits.
111 | PEMT | Power Quality | Evaluation of current harmonics at POI (Harmonic Load Flow model) | P=0.9; | HVRT Target Voltage (pu): P=0.9; Evaluation of current harmonics at POI (Harmonic Load Flow model); P=0.9 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Power Quality / Harmonic Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach harmonic load flow results showing current harmonic spectrum at POI for each active power level. Verify TDD ≤1.5% and band limits per CEA connectivity standards. ▶ File Name (Sim): Provide 'test.pscx' PSCAD model file including harmonic injection sources. ▶ Key check: All harmonic distortion values must be within CEA Connectivity Standard limits.
112 | PEMT | Power Quality | Evaluation of current harmonics at POI (Harmonic Load Flow model) | P=0.8; | HVRT Target Voltage (pu): P=0.8; Evaluation of current harmonics at POI (Harmonic Load Flow model); P=0.8 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Power Quality / Harmonic Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach harmonic load flow results showing current harmonic spectrum at POI for each active power level. Verify TDD ≤1.5% and band limits per CEA connectivity standards. ▶ File Name (Sim): Provide 'test.pscx' PSCAD model file including harmonic injection sources. ▶ Key check: All harmonic distortion values must be within CEA Connectivity Standard limits.
113 | PEMT | Power Quality | Evaluation of current harmonics at POI (Harmonic Load Flow model) | P=0.7; | HVRT Target Voltage (pu): P=0.7; Evaluation of current harmonics at POI (Harmonic Load Flow model); P=0.7 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Power Quality / Harmonic Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach harmonic load flow results showing current harmonic spectrum at POI for each active power level. Verify TDD ≤1.5% and band limits per CEA connectivity standards. ▶ File Name (Sim): Provide 'test.pscx' PSCAD model file including harmonic injection sources. ▶ Key check: All harmonic distortion values must be within CEA Connectivity Standard limits.
114 | PEMT | Power Quality | Evaluation of current harmonics at POI (Harmonic Load Flow model) | P=0.6; | HVRT Target Voltage (pu): P=0.6; Evaluation of current harmonics at POI (Harmonic Load Flow model); P=0.6 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Power Quality / Harmonic Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach harmonic load flow results showing current harmonic spectrum at POI for each active power level. Verify TDD ≤1.5% and band limits per CEA connectivity standards. ▶ File Name (Sim): Provide 'test.pscx' PSCAD model file including harmonic injection sources. ▶ Key check: All harmonic distortion values must be within CEA Connectivity Standard limits.
115 | PEMT | Power Quality | Evaluation of current harmonics at POI (Harmonic Load Flow model) | P=0.5; | HVRT Target Voltage (pu): P=0.5; Evaluation of current harmonics at POI (Harmonic Load Flow model); P=0.5 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Power Quality / Harmonic Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach harmonic load flow results showing current harmonic spectrum at POI for each active power level. Verify TDD ≤1.5% and band limits per CEA connectivity standards. ▶ File Name (Sim): Provide 'test.pscx' PSCAD model file including harmonic injection sources. ▶ Key check: All harmonic distortion values must be within CEA Connectivity Standard limits.
116 | PEMT | Power Quality | Evaluation of current harmonics at POI (Harmonic Load Flow model) | P=0.4; | HVRT Target Voltage (pu): P=0.4; Evaluation of current harmonics at POI (Harmonic Load Flow model); P=0.4 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Power Quality / Harmonic Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach harmonic load flow results showing current harmonic spectrum at POI for each active power level. Verify TDD ≤1.5% and band limits per CEA connectivity standards. ▶ File Name (Sim): Provide 'test.pscx' PSCAD model file including harmonic injection sources. ▶ Key check: All harmonic distortion values must be within CEA Connectivity Standard limits.
117 | PEMT | Power Quality | Evaluation of current harmonics at POI (Harmonic Load Flow model) | P=0.3; | HVRT Target Voltage (pu): P=0.3; Evaluation of current harmonics at POI (Harmonic Load Flow model); P=0.3 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Power Quality / Harmonic Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach harmonic load flow results showing current harmonic spectrum at POI for each active power level. Verify TDD ≤1.5% and band limits per CEA connectivity standards. ▶ File Name (Sim): Provide 'test.pscx' PSCAD model file including harmonic injection sources. ▶ Key check: All harmonic distortion values must be within CEA Connectivity Standard limits.
118 | PEMT | Power Quality | Evaluation of current harmonics at POI (Harmonic Load Flow model) | P=0.2; | HVRT Target Voltage (pu): P=0.2; Evaluation of current harmonics at POI (Harmonic Load Flow model); P=0.2 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Power Quality / Harmonic Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach harmonic load flow results showing current harmonic spectrum at POI for each active power level. Verify TDD ≤1.5% and band limits per CEA connectivity standards. ▶ File Name (Sim): Provide 'test.pscx' PSCAD model file including harmonic injection sources. ▶ Key check: All harmonic distortion values must be within CEA Connectivity Standard limits.
119 | PEMT | Power Quality | Evaluation of current harmonics at POI (Harmonic Load Flow model) | P=0.1; | HVRT Target Voltage (pu): P=0.1; Evaluation of current harmonics at POI (Harmonic Load Flow model); P=0.1 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Power Quality / Harmonic Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach harmonic load flow results showing current harmonic spectrum at POI for each active power level. Verify TDD ≤1.5% and band limits per CEA connectivity standards. ▶ File Name (Sim): Provide 'test.pscx' PSCAD model file including harmonic injection sources. ▶ Key check: All harmonic distortion values must be within CEA Connectivity Standard limits.
120 | PEMT | Power Quality | DC Current injection at POI | P=1.0; Q=0 | HVRT Target Voltage (pu): P=1.0; Q=0; DC Current injection at POI; P=1.0; Q=0 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Power Quality / Harmonic Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach harmonic load flow results showing current harmonic spectrum at POI for each active power level. Verify TDD ≤1.5% and band limits per CEA connectivity standards. ▶ File Name (Sim): Provide 'test.pscx' PSCAD model file including harmonic injection sources. ▶ Key check: All harmonic distortion values must be within CEA Connectivity Standard limits.
121 | PEMT | Power Quality | Flicker study at POI (Pst & Plt) | P=1.0; Q=0 | HVRT Target Voltage (pu): P=1.0; Q=0; Flicker study at POI (Pst & Plt); P=1.0; Q=0 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Power Quality / Harmonic Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach harmonic load flow results showing current harmonic spectrum at POI for each active power level. Verify TDD ≤1.5% and band limits per CEA connectivity standards. ▶ File Name (Sim): Provide 'test.pscx' PSCAD model file including harmonic injection sources. ▶ Key check: All harmonic distortion values must be within CEA Connectivity Standard limits.
122 | PEMT | Steady State | Reactive power capability test | POI Voltage(pu): 0.95; Supplemental device(if any) : In Service | HVRT Target Voltage (pu): 0.95; Duration of voltage dip (sec): In service; Reactive power capability test | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Reactive Power Capability Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.pscx' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
123 | PEMT | Steady State | Reactive power capability test | POI Voltage(pu): 1.05; Supplemental device(if any) : In Service | HVRT Target Voltage (pu): 1.05; Duration of voltage dip (sec): In service; Reactive power capability test | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Reactive Power Capability Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.pscx' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
124 | PEMT | Steady State | Reactive power capability test | POI Voltage(pu): 0.95; Supplemental device(if any) : Out of Service | HVRT Target Voltage (pu): 0.95; Duration of voltage dip (sec): Out of service; Reactive power capability test | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Reactive Power Capability Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.pscx' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
125 | PEMT | Steady State | Reactive power capability test | POI Voltage(pu): 1.05; Supplemental device(if any) :Out of Service | HVRT Target Voltage (pu): 1.05; Duration of voltage dip (sec): Out of service; Reactive power capability test | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Reactive Power Capability Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.pscx' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
126 | PEMT | Dynamic | Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 47.5; Active Power dispatch (pu): P=1.0; POI Voltage (pu): 1; Power factor (pf): Any; PPC Frequency Flag = Off | Frequency change (Hz): 50 to 47.5; Active Power dispatch (pu): P=1.0; POI Voltage (pu): 1; Power factor (pf): Any; Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation; P=1.0 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
127 | PEMT | Dynamic | Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation | Frequency change (Hz): 47.5Hz to 52Hz; Active Power dispatch (pu): P=1.0; POI Voltage (pu): 1; Power factor (pf): Any; PPC Frequency Flag = Off | Frequency change (Hz): 50 to 52; Active Power dispatch (pu): P=1.0; POI Voltage (pu): 1; Power factor (pf): Any; Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation; P=1.0 | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
128 | PEMT | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 49.50; POI Voltage (pu): 0.95; Power factor (pf): 0.95 lagging; Active Power dispatch (pu): 1; PPC Frequency Flag: Off | Frequency change (Hz): 50 to 49.50; POI Voltage (pu): 0.95; Power factor (pf): 0.95 lagging; Active Power dispatch (pu): 1; Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation; 0.95 lagging | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
129 | PEMT | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 49.50; POI Voltage (pu): 1.05; Power factor (pf): 0.95 leading; Active Power dispatch (pu): 1; PPC Frequency Flag: Off | POI Voltage (pu): 1.05; Power factor (pf): 0.95 leading; 0.95 leading | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
130 | PEMT | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 50.50; POI Voltage (pu): 0.95; Power factor (pf): 0.95 lagging; Active Power dispatch (pu): 1; PPC Frequency Flag: Off | Frequency change (Hz): 50 to 50.50; POI Voltage (pu): 0.95; Power factor (pf): 0.95 lagging; 0.95 lagging | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
131 | PEMT | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 50.50; POI Voltage (pu): 1.05; Power factor (pf): 0.95 leading; Active Power dispatch (pu): 1; PPC Frequency Flag: Off | POI Voltage (pu): 1.05; Power factor (pf): 0.95 leading; 0.95 leading | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
132 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced Three phase; Low voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
133 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced Three phase; Low voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
134 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced Three phase; Low voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
135 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced(LL); | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced(LL); Low voltage ride through; Unbalanced(LL) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
136 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced(LL); | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced(LL); Low voltage ride through; Unbalanced(LL) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
137 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced(LL); | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced(LL); Low voltage ride through; Unbalanced(LL) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
138 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced(LG); | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced(LG); Low voltage ride through; Unbalanced(LG) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
139 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced(LG); | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced(LG); Low voltage ride through; Unbalanced(LG) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
140 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced(LG); | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Unbalanced(LG); Low voltage ride through; Unbalanced(LG) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
141 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced Three phase; Low voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
142 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced Three phase; Low voltage ride through; Balanced Three phase | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced Three phase; Low voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
143 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced Three phase; Low voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
144 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced(LL); | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced(LL); Low voltage ride through; Unbalanced(LL) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
145 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced(LL); | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced(LL); Low voltage ride through; Unbalanced(LL) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
146 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced(LL); | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced(LL); Low voltage ride through; Unbalanced(LL) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
147 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced(LG); | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced(LG); Low voltage ride through; Unbalanced(LG) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
148 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced(LG); | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced(LG); Low voltage ride through; Unbalanced(LG) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
149 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced(LG); | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Unbalanced(LG); Low voltage ride through; Unbalanced(LG) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
150 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced Three phase; Low voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
151 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced Three phase; Low voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
152 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced Three phase; | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced Three phase; Low voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
153 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced(LL); | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced(LL); Low voltage ride through; Unbalanced(LL) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
154 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced(LL); | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced(LL); Low voltage ride through; Unbalanced(LL) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
155 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced(LL); Low voltage ride through; Unbalanced(LL) | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced(LL); Low voltage ride through; Unbalanced(LL) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
156 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced(LG); | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced(LG); Low voltage ride through; Unbalanced(LG) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
157 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced(LG); | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced(LG); Low voltage ride through; Unbalanced(LG) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
158 | PEMT | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced(LG); | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Unbalanced(LG); Low voltage ride through; Unbalanced(LG) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | LVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.pscx'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
159 | PEMT | Dynamic | Rate of change of active power: | Change in active power dispatch: Active power set-point and Ramp up test (ramp rate < 10% per minute); POI Voltage (pu): 1; Power factor (pf): Unity; | Change in active power dispatch: Active power set-point and Ramp up test (ramp rate < 10% per minute); POI Voltage (pu): 1; Power factor (pf): Unity; Rate of change of active power:; Active power set-point and Ramp up test (ramp rate < 10% per minute) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Ramp Rate / Active Power Set-point Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing ramp-up/ramp-down power response over time. Plot must show ramp rate (MW/min) and confirm it is ≤10% of rated per minute. ▶ File Name (Sim): Provide 'test.pscx' model file for this ramp test. ▶ Key check: Ramp rate ≤10% of rated MW per minute as required by CEA/Grid Code.
160 | PEMT | Dynamic | Rate of change of active power: | Change in active power dispatch: Active power set-point and Ramp down test (ramp rate < 10% per minute); POI Voltage (pu): 1; Power factor (pf): Unity; | Change in active power dispatch: Active power set-point and Ramp down test (ramp rate < 10% per minute); POI Voltage (pu): 1; Power factor (pf): Unity; Rate of change of active power:; Active power set-point and Ramp down test (ramp rate < 10% per minute) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Ramp Rate / Active Power Set-point Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing ramp-up/ramp-down power response over time. Plot must show ramp rate (MW/min) and confirm it is ≤10% of rated per minute. ▶ File Name (Sim): Provide 'test.pscx' model file for this ramp test. ▶ Key check: Ramp rate ≤10% of rated MW per minute as required by CEA/Grid Code.
161 | PEMT | Dynamic | Frequency response test (any droop in range of 3 - 6%): | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 1; POI Voltage (pu): 1; Power factor (pf): Unity; PPC Frequency Flag: On | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 1; POI Voltage (pu): 1; Power factor (pf): Unity; Frequency response test (any droop in range of 3 - 6%): | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
162 | PEMT | Dynamic | Frequency response test (any droop in range of 3 - 6%): | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 0.5; POI Voltage (pu): 1; Power factor (pf): Unity; PPC Frequency Flag: On | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 0.5; POI Voltage (pu): 1; Power factor (pf): Unity; Frequency response test (any droop in range of 3 - 6%): | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
163 | PEMT | Dynamic | Frequency response test (any droop in range of 3 - 6%): | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 0.1; POI Voltage (pu): 1; Power factor (pf): Unity; PPC Frequency Flag: On | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 0.1; POI Voltage (pu): 1; Power factor (pf): Unity; Frequency response test (any droop in range of 3 - 6%): | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
164 | PEMT | Dynamic | Frequency response test (any droop in range of 3 - 6%): | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 1; POI Voltage (pu): 1; Power factor (pf): Unity; PPC Frequency Flag: On | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 1; POI Voltage (pu): 1; Power factor (pf): Unity; Frequency response test (any droop in range of 3 - 6%): | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
165 | PEMT | Dynamic | Frequency response test (any droop in range of 3 - 6%): | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 0.5; POI Voltage (pu): 1; Power factor (pf): Unity; PPC Frequency Flag: On | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 0.5; POI Voltage (pu): 1; Power factor (pf): Unity; Frequency response test (any droop in range of 3 - 6%): | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
166 | PEMT | Dynamic | Frequency response test (any droop in range of 3 - 6%): | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 0.1; POI Voltage (pu): 1; Power factor (pf): Unity; PPC Frequency Flag: On | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 0.1; POI Voltage (pu): 1; Power factor (pf): Unity; Frequency response test (any droop in range of 3 - 6%): | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
167 | PEMT | Dynamic | Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz: | Change in frequency (Hz): Greater than 0.3Hz (upwards); Active Power dispatch (pu): 0.9; POI Voltage (pu): 1; Power factor (pf): Unity; | Change in frequency (Hz): Greater than 0.3Hz (upwards); Active Power dispatch (pu): 0.9; POI Voltage (pu): 1; Power factor (pf): Unity; Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz:; Greater than 0.3Hz (upwards) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
168 | PEMT | Dynamic | Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz: | Change in frequency (Hz): Greater than 0.3Hz (downwards); Active Power dispatch (pu): 0.9; POI Voltage (pu): 1; Power factor (pf): Unity; | Change in frequency (Hz): Greater than 0.3Hz (downwards); Active Power dispatch (pu): 0.9; POI Voltage (pu): 1; Power factor (pf): Unity; Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz:; Greater than 0.3Hz (downwards) | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.pscx' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
169 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced Three phase; | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced Three phase; High voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
170 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced Three phase; | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced Three phase; High voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
171 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced Three phase; | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced Three phase; High voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
172 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Single phase; | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Single phase; High voltage ride through; Single phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
173 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Single phase; | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Single phase; High voltage ride through; Single phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
174 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Single phase; | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Single phase; High voltage ride through; Single phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
175 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced Three phase; | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced Three phase; High voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
176 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced Three phase; | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced Three phase; High voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
177 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced Three phase; | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced Three phase; High voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
178 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Single phase; | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Single phase; High voltage ride through; Single phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
179 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Single phase; High voltage ride through; Single phase | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Single phase; High voltage ride through; Single phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
180 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Single phase; | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Single phase; High voltage ride through; Single phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
181 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Balanced Three phase; | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Balanced Three phase; High voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
182 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Balanced Three phase; | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Balanced Three phase; High voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
183 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Balanced Three phase; | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Balanced Three phase; High voltage ride through; Balanced Three phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
184 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Single phase; | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Single phase; High voltage ride through; Single phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
185 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Single phase; | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Single phase; High voltage ride through; Single phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
186 | PEMT | Dynamic | High voltage ride through | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Single phase; | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 0.25; Nature of voltage rise: Single phase; High voltage ride through; Single phase | EMT | TC_026_RMS_Results.pdf | No | Missing: TC_026_RMS_Results.pdf | test.pscx | Yes | Found | Yes |  | HVRT Test ¦ Level: PEMT ¦ Domain: EMT ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.pscx' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
187 | PRMS | Dynamic | Reactive power capability test: | POI Voltage (pu): 1; Supplemental devices(SVC/STATCOM)(if any): In - service(if installed) | HVRT Target Voltage (pu): 1; Duration of voltage rise (sec): In-service (If installed); Reactive power capability test: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | RPCT_W_Compensation_V_1_pf_1.sav | Yes | Found | Yes |  | Reactive Power Capability Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.sav' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
188 | PRMS | Dynamic | Reactive power capability test: | POI Voltage (pu): 0.95; Supplemental devices(SVC/STATCOM)(if any): In - service(if installed) | HVRT Target Voltage (pu): 0.95; Duration of voltage rise (sec): In-service (If installed); Reactive power capability test: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | RPCT_W_Compensation_V_095_pf_1.sav | No | Missing: RPCT_W_Compensation_V_095_pf_1.sav | Yes |  | Reactive Power Capability Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.sav' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
189 | PRMS | Dynamic | Reactive power capability test: | POI Voltage (pu): 1.05; Supplemental devices(SVC/STATCOM)(if any): In - service(if installed) | HVRT Target Voltage (pu): 1.05; Duration of voltage rise (sec): In-service (If installed); Reactive power capability test: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | RPCT_W_Compensation_V_1.05_pf_1.sav | Yes | Found | Yes |  | Reactive Power Capability Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.sav' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
190 | PRMS | Dynamic | Reactive power capability test: | POI Voltage (pu): 1; Supplemental devices(SVC/STATCOM)(if any): Out of service | HVRT Target Voltage (pu): 1; Duration of voltage rise (sec): Out of service; Reactive power capability test: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | RPCT_WO_Compensation_V_1_pf_1.sav | No | Missing: RPCT_WO_Compensation_V_1_pf_1.sav | Yes |  | Reactive Power Capability Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.sav' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
191 | PRMS | Dynamic | Reactive power capability test: | POI Voltage (pu): 0.95; Supplemental devices(SVC/STATCOM)(if any):Out of service | HVRT Target Voltage (pu): 0.95; Duration of voltage rise (sec): Out of service; Reactive power capability test: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | RPCT_WO_Compensation_V_095_pf_1.sav | No | Missing: RPCT_WO_Compensation_V_095_pf_1.sav | Yes |  | Reactive Power Capability Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.sav' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
192 | PRMS | Dynamic | Reactive power capability test: | POI Voltage (pu): 1.05; Supplemental devices(SVC/STATCOM)(if any): Out of service | HVRT Target Voltage (pu): 1.05; Duration of voltage rise (sec): Out of service; Reactive power capability test: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | RPCT_W0_Compensation_V_1.05_pf_1.sav | No | Missing: RPCT_W0_Compensation_V_1.05_pf_1.sav | Yes |  | Reactive Power Capability Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation results showing maximum capacitive and inductive reactive power at specified POI voltage. Supplemental devices (SVG/STATCOM) must be modelled as 'In Service' or 'Out of Service' per test parameters. ▶ File Name (Sim): Provide 'test.sav' model file with supplemental device status as specified. ▶ Key check: Plant must demonstrate full ±Q range per PQ capability curve.
193 | PRMS | Dynamic | Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 47.5; Default Active Power dispatch (pu): 1; POI Voltage (pu): 1; PPC Frequency Flag: Off; | Frequency change (Hz): 50 to 47.5; Default Active Power dispatch (pu): 1; POI Voltage (pu): 1; PPC Frequency Flag: Off; Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_47.5Hz_V_1_P_1_pf_1.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
194 | PRMS | Dynamic | Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 52; Default Active Power dispatch (pu): 1; POI Voltage (pu): 1; PPC Frequency Flag: Off; | Frequency change (Hz): 50 to 52; Capability to operate in frequency range: 47.5Hz to 52Hz with +/-5% voltage variation | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_52Hz_V_1_P_1_pf_1.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
195 | PRMS | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 49.5; POI Voltage (pu): 0.95; Power factor (pf): Lagging (0.95); Active Power dispatch (pu): 1; PPC Frequency Flag: Off | Frequency change (Hz): 50 to 49.5; POI Voltage (pu): 0.95; Power factor (pf): Lagging (0.95); Active Power dispatch (pu): 1; Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation; Lagging (0.95) | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_49.5Hz_V_0.95_P_1_pf_0.95.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
196 | PRMS | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 49.5; POI Voltage (pu): 1.05; Power factor (pf): Leading (0.95); Active Power dispatch (pu): 1; PPC Frequency Flag: Off | POI Voltage (pu): 1.05pu; Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_49.5Hz_V_1.05_P_1_pf_-0.95.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
197 | PRMS | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 50.5; POI Voltage (pu): 0.95; Power factor (pf): Lagging (0.95); Active Power dispatch (pu): 1; PPC Frequency Flag: Off | Frequency change (Hz): 50 to 50.5; POI Voltage (pu): 0.95pu; Power factor (pf): Lagging (0.95); Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation; Lagging (0.95) | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_50.5Hz_V_0.95_P_1_pf_0.95.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
198 | PRMS | Dynamic | Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | Frequency change (Hz): 50 to 50.5; POI Voltage (pu): 1.05; Power factor (pf): Leading (0.95); Active Power dispatch (pu): 1; PPC Frequency Flag: Off | POI Voltage (pu): 1.05pu; Capability to provide rated output in frequency range of 49.5Hz to 50.5Hz with +/-5% voltage variation | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_50.5Hz_V_1.05_P_1_pf_-0.95.sav | Yes | Found | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
199 | PRMS | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced; | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced; Low voltage ride through; Balanced | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | LVRT_0.85_P_100%.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
200 | PRMS | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced; | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Low voltage ride through | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | LVRT_0.5_P_100%.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
201 | PRMS | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec):0.3; Pre-fault Active Power dispatch (pu): 1; Nature of voltage dip: Balanced; | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Low voltage ride through | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | LVRT_0.15_P_100%.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
202 | PRMS | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced; | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.5; Low voltage ride through | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | LVRT_0.85_P_50%.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
203 | PRMS | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced; | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Low voltage ride through | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | LVRT_0.5_P_50%.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
204 | PRMS | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec):0.3; Pre-fault Active Power dispatch (pu): 0.5; Nature of voltage dip: Balanced; | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Low voltage ride through | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | LVRT_0.15_P_50%.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
205 | PRMS | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced; | LVRT Target Voltage (pu): 0.85; Duration of voltage dip (sec): 3; Pre-fault Active Power dispatch (pu): 0.25; Low voltage ride through | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | LVRT_0.85_P_25%.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
206 | PRMS | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced; | LVRT Target Voltage (pu): 0.5; Duration of voltage dip (sec): 1.65; Low voltage ride through | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | LVRT_0.5_P_25%.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
207 | PRMS | Dynamic | Low voltage ride through | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec):0.3; Pre-fault Active Power dispatch (pu): 0.25; Nature of voltage dip: Balanced; | LVRT Target Voltage (pu): 0.15; Duration of voltage dip (sec): 0.3; Low voltage ride through | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | LVRT_0.15_P_25%.sav | Yes | Found | Yes |  | LVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach the corresponding PSCAD/PSS/E simulation output report showing voltage, active power (P), reactive power (Q), Id, and Iq time-domain plots for this specific test case. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. Ensure plots clearly show pre-fault, during-fault, and post-fault periods. ▶ File Name (Sim): Provide the simulation model file used – 'test.sav'. For PSS/E: .SAV + .DYR file; for PSCAD: .pscx/.pswx file. File should reproduce the exact test case documented in the report. ▶ Key checks: No inverter tripping, ΔIq > 0 during fault, active power recovers ≥90% within 1 sec of clearance.
208 | PRMS | Dynamic | Active power set-point and Rate of change of active power | Active power set-point and Ramp up test (rate < 10% per minute) POI Voltage (pu): 1; Power factor (pf): Unity; | Change in active power dispatch: Active power set-point and Ramp up test (rate < 10% per minute); POI Voltage (pu): 1; Power factor (pf): Unity; Active power set-point and Rate of change of active power; Active power set-point and Ramp up test (rate < 10% per minute) | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Ramp Up.sav | No | Missing: Ramp Up.sav | Yes |  | Ramp Rate / Active Power Set-point Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing ramp-up/ramp-down power response over time. Plot must show ramp rate (MW/min) and confirm it is ≤10% of rated per minute. ▶ File Name (Sim): Provide 'test.sav' model file for this ramp test. ▶ Key check: Ramp rate ≤10% of rated MW per minute as required by CEA/Grid Code.
209 | PRMS | Dynamic | Active power set-point and Rate of change of active power | Active power set-point and Ramp down test (ramp rate < 10% per minute) POI Voltage (pu): 1; Power factor (pf): Unity; | Change in active power dispatch: Active power set-point and Ramp down test (ramp rate < 10% per minute); Active power set-point and Rate of change of active power; Active power set-point and Ramp down test (ramp rate < 10% per minute) | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Ramp Down.sav | No | Missing: Ramp Down.sav | Yes |  | Ramp Rate / Active Power Set-point Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing ramp-up/ramp-down power response over time. Plot must show ramp rate (MW/min) and confirm it is ≤10% of rated per minute. ▶ File Name (Sim): Provide 'test.sav' model file for this ramp test. ▶ Key check: Ramp rate ≤10% of rated MW per minute as required by CEA/Grid Code.
210 | PRMS | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 1; POI Voltage (pu): 1; Power factor (pf): Unity; PPC Frequency Flag: On | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 1; POI Voltage (pu): 1; Power factor (pf): Unity; Frequency response test (any droop in range of 3 - 6%) | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_50.03-50.15Hz_P_1.sav | No | Missing: Freq_50.03-50.15Hz_P_1.sav | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
211 | PRMS | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 0.5; POI Voltage (pu): 1; Power factor (pf): Unity; PPC Frequency Flag: On | Active Power dispatch (pu): 0.5; Frequency response test (any droop in range of 3 - 6%) | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_50.03-50.15Hz_P_0.5.sav | No | Missing: Freq_50.03-50.15Hz_P_0.5.sav | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
212 | PRMS | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency change (Hz): 50 to 50.15; Active Power dispatch (pu): 0.1; POI Voltage (pu): 1; Power factor (pf): Unity; PPC Frequency Flag: On | Active Power dispatch (pu): 0.1; Frequency response test (any droop in range of 3 - 6%) | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_50.03-50.15Hz_P_0.1.sav | No | Missing: Freq_50.03-50.15Hz_P_0.1.sav | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
213 | PRMS | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 1; POI Voltage (pu): 1; Power factor (pf): Unity; PPC Frequency Flag: On | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 1; Frequency response test (any droop in range of 3 - 6%) | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_49.97-49.85Hz_P_1.sav | No | Missing: Freq_49.97-49.85Hz_P_1.sav | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
214 | PRMS | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 0.5; POI Voltage (pu): 1; Power factor (pf): Unity; PPC Frequency Flag: On | Active Power dispatch (pu): 0.5; Frequency response test (any droop in range of 3 - 6%) | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_49.97-49.85Hz_P_0.5.sav | No | Missing: Freq_49.97-49.85Hz_P_0.5.sav | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
215 | PRMS | Dynamic | Frequency response test (any droop in range of 3 - 6%) | Frequency change (Hz): 50 to 49.85; Active Power dispatch (pu): 0.1; POI Voltage (pu): 1; Power factor (pf): Unity; PPC Frequency Flag: On | Active Power dispatch (pu): 0.1; Frequency response test (any droop in range of 3 - 6%) | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_49.97-49.85Hz_P_0.1.sav | No | Missing: Freq_49.97-49.85Hz_P_0.1.sav | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
216 | PRMS | Dynamic | Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz: | Change in frequency (Hz): Greater than 0.3Hz (upwards); Default Active Power dispatch (pu): 0.9; POI Voltage (pu): 1; Power factor (pf): Unity; |  | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_49.5Hz_P_0.9.sav | No | Missing: Freq_49.5Hz_P_0.9.sav | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
217 | PRMS | Dynamic | Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz: | Greater than 0.3Hz (downwards) Default Active Power dispatch (pu): 0.9; POI Voltage (pu): 1; Power factor (pf): Unity; | Change in frequency (Hz): Greater than 0.3Hz (downwards); Demonstration of immediate (within 1 second) real power primary frequency response of at least 10% of maximum Alternating Current active power capacity for frequency deviation in excess of 0.3 Hz:; Greater than 0.3Hz (downwards) | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | Freq_50.5Hz_P_0.9.sav | No | Missing: Freq_50.5Hz_P_0.9.sav | Yes |  | Frequency Response Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing frequency step and corresponding active power response. Include time plots for frequency (Hz) and P (pu). Droop response must be visible within the configured dead-band. ▶ File Name (Sim): Provide 'test.sav' model file configured with PPC frequency flag ON for this test. ▶ Key check: Droop must be in range 3%–6%; FFR tests require ≥10% P response within 1 second for ¦Δf¦ > 0.3 Hz.
218 | PRMS | Dynamic | High voltage ride through: | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced; | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced; High voltage ride through:; Balanced | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | HVRT_1.1_P_100%.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
219 | PRMS | Dynamic | High voltage ride through: | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced; | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; High voltage ride through: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | HVRT_1.1_P_50%.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
220 | PRMS | Dynamic | High voltage ride through: | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 1; Nature of voltage rise: Balanced; | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; High voltage ride through: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | HVRT_1.1_P_25%.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
221 | PRMS | Dynamic | High voltage ride through: | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced; | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.5; High voltage ride through: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | HVRT_1.2_P_100%.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
222 | PRMS | Dynamic | High voltage ride through: | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced; | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; High voltage ride through: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | HVRT_1.2_P_50%.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
223 | PRMS | Dynamic | High voltage ride through: | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced; | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; High voltage ride through: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | HVRT_1.2_P_25%.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
224 | PRMS | Dynamic | High voltage ride through: | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.5; Nature of voltage rise: Balanced; | HVRT Target Voltage (pu): 1.3; Duration of voltage rise (sec): 0.2; Initial Active Power dispatch (pu): 0.2; High voltage ride through: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | HVRT_1.3_P_100%.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
225 | PRMS | Dynamic | High voltage ride through: | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; Initial Active Power dispatch (pu): 0.2; Nature of voltage rise: Balanced; | HVRT Target Voltage (pu): 1.2; Duration of voltage rise (sec): 2; High voltage ride through: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | HVRT_1.3_P_50%.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
226 | PRMS | Dynamic | High voltage ride through: | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; Initial Active Power dispatch (pu): 0.2; Nature of voltage rise: Balanced; | HVRT Target Voltage (pu): 1.1; Duration of voltage rise (sec): Continuous; High voltage ride through: | RMS | 1000 MW Serentica_Hybrid,Solapur PSSE Model Study Report_V00 | Yes | Found | HVRT_1.3_P_25%.sav | Yes | Found | Yes |  | HVRT Test ¦ Level: PRMS ¦ Domain: RMS ▶ File Name (PDF): Attach simulation output showing voltage, P, Q, Id, Iq time plots for this HVRT case. Verify inverter absorbs reactive power (negative ΔIq) during voltage rise. Format: 'TC_<NNN>_<RMS/EMT>_Results.pdf'. ▶ File Name (Sim): Provide 'test.sav' model file replicating this exact HVRT scenario. ▶ Key checks: No tripping, reactive absorption as per K-factor, active power maintained.
|  |  | Row Labels | Count of Unit level(UIBR), USVG/Plant level(P)
|  |  | PEMT | 77
|  |  | PRMS | 40
|  |  | UIBR | 90
|  |  | USVG | 19
|  |  | Grand Total | 226
The Applicant is required to fill in yellow-highlighted cells only. All remaining fields are system-locked and pre-populated for reference.
Note on I4: Missing: - TC_001_RMS_Results.pdf
Note on I5: Missing: - TC_002_RMS_Results.pdf
Note on I6: Missing: - TC_003_RMS_Results.pdf
Note on I7: Missing: - TC_004_RMS_Results.pdf
Note on I8: Missing: - TC_005_RMS_Results.pdf
Note on I9: Missing: - TC_006_RMS_Results.pdf
Note on I10: Missing: - TC_007_RMS_Results.pdf
Note on I11: Missing: - TC_008_RMS_Results.pdf
Note on I12: Missing: - TC_009_RMS_Results.pdf
Note on I13: Missing: - TC_010_RMS_Results.pdf
Note on I14: Missing: - TC_011_RMS_Results.pdf
Note on I15: Missing: - TC_012_RMS_Results.pdf
Note on I16: Missing: - TC_013_RMS_Results.pdf
Note on I17: Missing: - TC_014_RMS_Results.pdf
Note on I18: Missing: - TC_015_RMS_Results.pdf
Note on I19: Missing: - TC_016_RMS_Results.pdf
Note on I20: Missing: - TC_017_RMS_Results.pdf
Note on I21: Missing: - TC_018_RMS_Results.pdf
Note on I22: Missing: - TC_019_RMS_Results.pdf
Note on I23: Missing: - TC_020_RMS_Results.pdf
Note on I24: Missing: - TC_021_RMS_Results.pdf
Note on I25: Missing: - TC_022_RMS_Results.pdf
Note on I26: Missing: - TC_023_RMS_Results.pdf
Note on I27: Missing: - TC_024_RMS_Results.pdf
Note on I28: Missing: - TC_025_RMS_Results.pdf
Note on I29: Missing: - TC_026_RMS_Results.pdf
Note on I30: Missing: - TC_027_RMS_Results.pdf
Note on I31: Missing: - TC_028_RMS_Results.pdf
Note on I32: Missing: - TC_029_RMS_Results.pdf
Note on I33: Missing: - TC_030_RMS_Results.pdf
Note on I34: Missing: - TC_031_RMS_Results.pdf
Note on I35: Missing: - TC_032_RMS_Results.pdf
Note on I36: Missing: - TC_033_RMS_Results.pdf
Note on I37: Missing: - TC_034_EMT_Results.pdf
Note on I38: Missing: - TC_035_EMT_Results.pdf
Note on I39: Missing: - TC_036_EMT_Results.pdf
Note on I40: Missing: - TC_037_EMT_Results.pdf
Note on I41: Missing: - TC_038_EMT_Results.pdf
Note on I42: Missing: - TC_039_EMT_Results.pdf
Note on I43: Missing: - TC_040_EMT_Results.pdf
Note on I44: Missing: - TC_041_EMT_Results.pdf
Note on I45: Missing: - TC_042_EMT_Results.pdf
Note on I46: Missing: - TC_043_EMT_Results.pdf
Note on I47: Missing: - TC_044_EMT_Results.pdf
Note on I48: Missing: - TC_045_EMT_Results.pdf
Note on I49: Missing: - TC_046_EMT_Results.pdf
Note on I50: Missing: - TC_047_EMT_Results.pdf
Note on I51: Missing: - TC_048_EMT_Results.pdf
Note on I52: Missing: - TC_049_EMT_Results.pdf
Note on I53: Missing: - TC_050_EMT_Results.pdf
Note on I54: Missing: - TC_051_EMT_Results.pdf
Note on I55: Missing: - TC_052_EMT_Results.pdf
Note on I56: Missing: - TC_053_EMT_Results.pdf
Note on I57: Missing: - TC_054_EMT_Results.pdf
Note on I58: Missing: - TC_055_EMT_Results.pdf
Note on I59: Missing: - TC_056_EMT_Results.pdf
Note on I60: Missing: - TC_057_EMT_Results.pdf
Note on I61: Missing: - TC_058_EMT_Results.pdf
Note on I62: Missing: - TC_059_EMT_Results.pdf
Note on I63: Missing: - TC_060_EMT_Results.pdf
Note on I64: Missing: - TC_061_EMT_Results.pdf
Note on I65: Missing: - TC_062_EMT_Results.pdf
Note on I66: Missing: - TC_063_EMT_Results.pdf
Note on I67: Missing: - TC_064_EMT_Results.pdf
Note on I68: Missing: - TC_065_EMT_Results.pdf
Note on I69: Missing: - TC_066_EMT_Results.pdf
Note on I70: Missing: - TC_067_EMT_Results.pdf
Note on I71: Missing: - TC_068_EMT_Results.pdf
Note on I72: Missing: - TC_069_EMT_Results.pdf
Note on I73: Missing: - TC_070_EMT_Results.pdf
Note on I74: Missing: - TC_071_EMT_Results.pdf
Note on I75: Missing: - TC_072_EMT_Results.pdf
Note on I76: Missing: - TC_073_EMT_Results.pdf
Note on I77: Missing: - TC_074_EMT_Results.pdf
Note on I78: Missing: - TC_075_EMT_Results.pdf
Note on I79: Missing: - TC_076_EMT_Results.pdf
Note on I80: Missing: - TC_077_EMT_Results.pdf
Note on I81: Missing: - TC_078_EMT_Results.pdf
Note on I82: Missing: - TC_079_EMT_Results.pdf
Note on I83: Missing: - TC_080_EMT_Results.pdf
Note on I84: Missing: - TC_001_RMS_Results.pdf
Note on I85: Missing: - TC_002_RMS_Results.pdf
Note on I86: Missing: - TC_003_RMS_Results.pdf
Note on I87: Missing: - TC_004_RMS_Results.pdf
Note on I88: Missing: - TC_005_RMS_Results.pdf
Note on I89: Missing: - TC_006_RMS_Results.pdf
Note on I90: Missing: - TC_007_RMS_Results.pdf
Note on I91: Missing: - TC_008_RMS_Results.pdf
Note on I92: Missing: - TC_009_RMS_Results.pdf
Note on I93: Missing: - TC_010_RMS_Results.pdf
Note on I94: Missing: - TC_011_RMS_Results.pdf
Note on I95: Missing: - TC_012_RMS_Results.pdf
Note on I96: Missing: - TC_013_RMS_Results.pdf
Note on I97: Missing: - TC_014_RMS_Results.pdf
Note on I98: Missing: - TC_015_RMS_Results.pdf
Note on I99: Missing: - TC_016_RMS_Results.pdf
Note on I100: Missing: - TC_017_RMS_Results.pdf
Note on I101: Missing: - TC_018_RMS_Results.pdf
Note on I102: Missing: - TC_019_RMS_Results.pdf
Note on I103: Missing: - TC_020_RMS_Results.pdf
Note on I104: Missing: - TC_021_RMS_Results.pdf
Note on I105: Missing: - TC_022_RMS_Results.pdf
Note on I106: Missing: - TC_023_RMS_Results.pdf
Note on I107: Missing: - TC_024_RMS_Results.pdf
Note on I108: Missing: - TC_025_RMS_Results.pdf
Note on I109: Missing: - TC_026_RMS_Results.pdf
Note on I110: Missing: - TC_026_RMS_Results.pdf
Note on I111: Missing: - TC_026_RMS_Results.pdf
Note on I112: Missing: - TC_026_RMS_Results.pdf
Note on I113: Missing: - TC_026_RMS_Results.pdf
Note on I114: Missing: - TC_026_RMS_Results.pdf
Note on I115: Missing: - TC_026_RMS_Results.pdf
Note on I116: Missing: - TC_026_RMS_Results.pdf
Note on I117: Missing: - TC_026_RMS_Results.pdf
Note on I118: Missing: - TC_026_RMS_Results.pdf
Note on I119: Missing: - TC_026_RMS_Results.pdf
Note on I120: Missing: - TC_026_RMS_Results.pdf
Note on I121: Missing: - TC_026_RMS_Results.pdf
Note on I122: Missing: - TC_026_RMS_Results.pdf
Note on I123: Missing: - TC_026_RMS_Results.pdf
Note on I124: Missing: - TC_026_RMS_Results.pdf
Note on I125: Missing: - TC_026_RMS_Results.pdf
Note on I126: Missing: - TC_026_RMS_Results.pdf
Note on I127: Missing: - TC_026_RMS_Results.pdf
Note on I128: Missing: - TC_026_RMS_Results.pdf
Note on I129: Missing: - TC_026_RMS_Results.pdf
Note on I130: Missing: - TC_026_RMS_Results.pdf
Note on I131: Missing: - TC_026_RMS_Results.pdf
Note on I132: Missing: - TC_026_RMS_Results.pdf
Note on I133: Missing: - TC_026_RMS_Results.pdf
Note on I134: Missing: - TC_026_RMS_Results.pdf
Note on I135: Missing: - TC_026_RMS_Results.pdf
Note on I136: Missing: - TC_026_RMS_Results.pdf
Note on I137: Missing: - TC_026_RMS_Results.pdf
Note on I138: Missing: - TC_026_RMS_Results.pdf
Note on I139: Missing: - TC_026_RMS_Results.pdf
Note on I140: Missing: - TC_026_RMS_Results.pdf
Note on I141: Missing: - TC_026_RMS_Results.pdf
Note on I142: Missing: - TC_026_RMS_Results.pdf
Note on I143: Missing: - TC_026_RMS_Results.pdf
Note on I144: Missing: - TC_026_RMS_Results.pdf
Note on I145: Missing: - TC_026_RMS_Results.pdf
Note on I146: Missing: - TC_026_RMS_Results.pdf
Note on I147: Missing: - TC_026_RMS_Results.pdf
Note on I148: Missing: - TC_026_RMS_Results.pdf
Note on I149: Missing: - TC_026_RMS_Results.pdf
Note on I150: Missing: - TC_026_RMS_Results.pdf
Note on I151: Missing: - TC_026_RMS_Results.pdf
Note on I152: Missing: - TC_026_RMS_Results.pdf
Note on I153: Missing: - TC_026_RMS_Results.pdf
Note on I154: Missing: - TC_026_RMS_Results.pdf
Note on I155: Missing: - TC_026_RMS_Results.pdf
Note on I156: Missing: - TC_026_RMS_Results.pdf
Note on I157: Missing: - TC_026_RMS_Results.pdf
Note on I158: Missing: - TC_026_RMS_Results.pdf
Note on I159: Missing: - TC_026_RMS_Results.pdf
Note on I160: Missing: - TC_026_RMS_Results.pdf
Note on I161: Missing: - TC_026_RMS_Results.pdf
Note on I162: Missing: - TC_026_RMS_Results.pdf
Note on I163: Missing: - TC_026_RMS_Results.pdf
Note on I164: Missing: - TC_026_RMS_Results.pdf
Note on I165: Missing: - TC_026_RMS_Results.pdf
Note on I166: Missing: - TC_026_RMS_Results.pdf
Note on I167: Missing: - TC_026_RMS_Results.pdf
Note on I168: Missing: - TC_026_RMS_Results.pdf
Note on I169: Missing: - TC_026_RMS_Results.pdf
Note on I170: Missing: - TC_026_RMS_Results.pdf
Note on I171: Missing: - TC_026_RMS_Results.pdf
Note on I172: Missing: - TC_026_RMS_Results.pdf
Note on I173: Missing: - TC_026_RMS_Results.pdf
Note on I174: Missing: - TC_026_RMS_Results.pdf
Note on I175: Missing: - TC_026_RMS_Results.pdf
Note on I176: Missing: - TC_026_RMS_Results.pdf
Note on I177: Missing: - TC_026_RMS_Results.pdf
Note on I178: Missing: - TC_026_RMS_Results.pdf
Note on I179: Missing: - TC_026_RMS_Results.pdf
Note on I180: Missing: - TC_026_RMS_Results.pdf
Note on I181: Missing: - TC_026_RMS_Results.pdf
Note on I182: Missing: - TC_026_RMS_Results.pdf
Note on I183: Missing: - TC_026_RMS_Results.pdf
Note on I184: Missing: - TC_026_RMS_Results.pdf
Note on I185: Missing: - TC_026_RMS_Results.pdf
Note on I186: Missing: - TC_026_RMS_Results.pdf
Note on I187: Missing: - TC_026_RMS_Results.pdf
Note on I188: Missing: - TC_026_RMS_Results.pdf
Note on I189: Missing: - TC_026_RMS_Results.pdf
Note on L191: Missing: - RPCT_W_Compensation_V_095_pf_1.sav
Note on L193: Missing: - RPCT_WO_Compensation_V_1_pf_1.sav
Note on L194: Missing: - RPCT_WO_Compensation_V_095_pf_1.sav
Note on L195: Missing: - RPCT_W0_Compensation_V_1.05_pf_1.sav
Note on L211: Missing: - Ramp Up.sav
Note on L212: Missing: - Ramp Down.sav
Note on L213: Missing: - Freq_50.03-50.15Hz_P_1.sav
Note on L214: Missing: - Freq_50.03-50.15Hz_P_0.5.sav
Note on L215: Missing: - Freq_50.03-50.15Hz_P_0.1.sav
Note on L216: Missing: - Freq_49.97-49.85Hz_P_1.sav
Note on L217: Missing: - Freq_49.97-49.85Hz_P_0.5.sav
Note on L218: Missing: - Freq_49.97-49.85Hz_P_0.1.sav
Note on L219: Missing: - Freq_49.5Hz_P_0.9.sav
Note on L220: Missing: - Freq_50.5Hz_P_0.9.sav

## Addl Checklist
Checklist for Prerequisites prior to Submission of Final Data
Sl No | Category | Checklist Item | Yes/No | Remarks | 📝 Developer Guidance / Explanatory Note
1 | Reactive Capability | No overloading observed in transformers / IDTs & any other elements | Yes |  | Confirm no transformer (power transformer or IDT) is overlo+F3:F19aded (>100% of nameplate rating) in any simulation scenario. Check thermal limit compliance at site temperature. Enter 'Yes' if no overloading observed.
| Reactive Capability | Load-Flow achieved using full-newton raphson method for the detailed Plant model | Yes |  | Confirm whether load-flow solutions are converged using Full-Newton Raphson method & verify the load-flow solution parameters considered/assumed in PSSE steady state report.
| Reactive Capability | Reactive power compensation is adequate | Yes |  | Verify that reactive power compensation (SVG, capacitor banks, or IBR reactive capability) is adequate to meet 0.95 pf lag to 0.95 pf lead requirement at POI under all voltage conditions. Enter 'Yes' if adequate.
| Power Quality | Power Quality Study has been revised with actual short circuit level and X/R ratio obtained from CTUIL | No
| Power Quality | Harmonic impedance scan plots at POI for with and without filter cases has been incorporated in the report. | No
| Power Quality | Confirm filters are also included in the plant level dynamic simulation models of PSSE & PSCAD | Yes | How to model Filter banks in dynamic PSSE model? As capacitor or, switched shunt? Does all IBR/WTG OEM also include unit level harmonic filter in PSSE/PSCAD? Are all power-transformer model in the dynamic model are also frequency dependent? How STATCOM at 33kV is modelled in PSCAD dynamic model, any series smoothing reactor available in SVG? | Ensure filters are modelled in plant level simulation models
| PFR/FFR | PFR controls can recommence after FFR response is delivered (fuel/resource availability = 100%) | No |  | Verify whether the Master PPC (primary frequency controller) is able to govern the control of active power as per the frequency droop after 10% active power response is achieved within 1 second for frequency deviations >0.3 Hz, considering all resource/fuel are available upto 1.0 pu
| PFR/FFR | Fast Frequency Response(FFR) response(> 0.3 Hz) is adequate | Yes |  | Verify Fast Frequency Response (FFR): Plant must inject/absorb ≥10% of rated active power within 1 second for ¦Δf¦ > 0.3 Hz. Check plots in dynamics report. Enter 'Yes' if compliant, 'No' if not.
| PFR/FFR | Primary Frequency Response(PFR) response is adequate | Yes |  | Verify Primary Frequency Response (PFR): Plant must respond proportionally to frequency deviation per configured droop (3%–6%). Response must be sustained as per the setting of frequency controller. Enter 'Yes' if demonstrated in frequency response test cases.
| PFR/FFR | Primary Frequency Response(PFR) sharing is proportional among generators/BESS inverters | Yes | Subjected to MPPC active power distribution philosophy, active power priority distribution philosophy can override IBR or, WTG or, BESS based upon MPPC commands. | Applicable if multiple generators or BESS inverters share PFR. Confirm that PFR sharing is proportional to each unit's rating (not biased to one unit). Enter 'Yes' if proportionality is demonstrated.. It is preferred option;
| Modelling | Unit Test report data matches simulation model data or data considered in unit level simulation models is directly taken from unit test reports. | Yes | Subjective, How to measure mismatch from unit level performance? Has FFR control philosophy been provided by OEM? | Compare values from the unit-level type test report with PSCAD simulation model data. Ensure all data particularly harmonics, dc offset data is taken from test reports. Enter 'Yes' if values are matching. If 'No', investigate discrepancy and update model.
| Modelling | OEM has certified which model parameters are tunable and non-tunable | Yes |  | Confirm OEM has provided a formal document certifying which inverter/WTG model parameters can be adjusted (tunable) and which are fixed (non-tunable / OEM-locked). Enter 'Yes' if document received. Critical for benchmarking compliance.
| Modelling | Parameters are consistent in simulation models PSSE, PSCAD & Reports(Eg: MVA, Xsource of Inverters & SVGs, R,X,B parameters of cables etc ) | Yes |  | Verify that the MVA base used in PSS/E and PSCAD models is identical and consistent with the plant rating. Common error: mismatch between reports & simulation models. Enter 'Yes' if consistent. Check all .DYR and .pscx files.
| Modelling | Transformer taps remain unchanged across scenarios | Yes |  | Verify that transformer tap positions are identical across all simulation scenarios (load flow cases). If taps change between cases, it must be justified. Enter 'Yes' if taps are consistent.
| Modelling | Unit level simulation models are consistent with actual test results | Yes |  | Confirm unit-level simulation models (PSS/E generic model / PSCAD detailed model) are validated against actual type test results. Validation report must show V, P, Q, Id, Iq comparison. Enter 'Yes' if validated.
| Modelling | Plant EMT model Initialization achieved appropriately in the simulation for all different active power levels | Yes |  | Confirm whether the plant model is able to initialise appropriately within 3-5 seconds (simulation time) & review the auxiliary power drawn by the plant during the process. Recommended practice.
| Modelling | Plant level dynamic simulation parameters, properties or assumptions used for the study is included in the respective report | Yes |  | PSSE & PSCAD Model parameters & assumptions are mentioned in the study reports in details
| LVRT/HVRT | PPC Enters into LVRT/HVRT conditions for all shallow fault cases | Yes |  | Run a dynamic simulation (PSCAD/PSS/E) with LVRT at 0.85 pu and HVRT 1.1 pu (symmetrical & asymmetrical) and verify PPC correctly switches to LVRT/HVRT mode. Enter 'Yes' if mode transition is correctly demonstrated.
| LVRT/HVRT | Id & Iq are monitored at PoI level under LVRT/HVRT reactive power flow conditions | Yes |  | Confirm that Id and Iq time-domain plots at POI level are included in the dynamics report for LVRT/HVRT cases. These plots validate reactive current injection compliance. Enter 'Yes' if plots are present and show correct behaviour.
| LVRT/HVRT | Plant performance is stable during LVRT/HVRT | Yes | Subjective, oscillations are expected for unbalanced conditions | Verify plant stability during LVRT/HVRT: No sustained oscillations in P, Q, V, or Id/Iq after fault clearance. Check time-domain plots for oscillation or divergence. Enter 'Yes' if stable post-fault response observed.
| LVRT/HVRT | Id & Iq control behaviour in plant simulation plots matches test report plots | Yes |  | Compare Id and Iq control behaviour time plots from plant-level PSCAD simulation vs. unit-level type test report for equivalent fault conditions. Enter 'Yes' if plots match in shape, magnitude, and timing (within ±10%).
| LVRT/HVRT | In case of unbalanced cases, dynamic simulation report shall also include Negative Sequence Currents & Negative Sequence voltage of IBR(including supplemental devices) and POI | Yes |  | Negative sequence currents & voltages should also be plotted at unit level & POI with appropriate scaling in per unit basis for respective equipment/plant MVA/Nameplate capacity.